## Q&A's sector
Q&A log on offshorewind.rvo.nl - Tender wind farm zone Borssele
Last update: 20160919
Number | Page | Subject | Sub subject | Question | Date response | Response
118 | General | Safety zones | Jack-up operations | We have noticed a discrepancy in the two responses provided in the Q&A log as regards safety zones and jack-up operations (Q&A 17 and 038). Can you clarify if jack-up operations within the 500 m safety zone are allowed during installation of the wind farm as well as during the operational phase for potential repair and maintenance works? | 2016-09-19 | Jack-up operations are allowed in your own safety zone but prohibited in a maintenance zone of an existing cable or pipe. When a safety zone overlaps a maintenance zone, jack-up operations are prohibited unless agreed otherwise in a proximity agreement.
117 | Studies | Metocean | Individual wave height distribution | The table presenting the individual wave height distribution for BWFZ sites II, III and IV seems to be inconsistent in terms of a) the total amount of waves and b) the wave steepness of certain presented conditions. Is this correct? | 2016-09-05 | The numbers in this table (‘under the tab ‘Individual_H_distribution’ at the ‘tables’ files ) for the three aforementioned sites will have to be divided by a factor 10,000. We have attached to this Q&A the corrected tables of each site separately. RVO is in contact with DNV GL regarding the possible consequences for the Statement of Compliance.The total sum of waves per site should then be as following: Site I : 9,319,060 (Metocean study for the Borssele Wind Farm Zone Individual H Distribution Tables Site I.xls). Site II : 9,370,395 (Metocean study for the Borssele Wind Farm Zone Individual H Distribution Tables Site II.xls). Site III : 9,313,575 (Metocean study for the Borssele Wind Farm Zone Individual H Distribution Tables Site III.xls). Site IV : 9,307,749 (Metocean study for the Borssele Wind Farm Zone Individual H Distribution Tables Site IV.xls).These are yearly averaged values. Multiplying the amount of waves with the determined averaged Tm0,2 of ~3.4s results in ~1 year. Additionally, a limited amount of waves are very - or even unrealistically - steep. It is suggested to set to zero the joint occurrences values in the tables when the wave steepness is above what is generally considered realistic: ~0.142.
116 | Studies | Metocean report | Extreme minimum water temperatures | The Metocean report clearly describes and illustrates the extreme high water temperature. What is to be considered for the extreme minimum water temperature? | 2016-08-26 | No analysis on extreme minimum water temperature has been conducted for Borssele. The following can be considered as input: In general the freezing point of saline water is ~ −2 °C with typical values of salinity ~30 ppt. However, due to the influence of the relative warm Gulf Stream and therefore the relative mild North Sea climate the minimum temperature of the sea water surface near BWFZ will be several degrees above ~ −2 °C. Following Figure 8.2 of the BWFZ Metocean reports this is confirmed showing that the water temperature does not drop below +2°C. The applied hindcast dataset (CFSR) provides similar values; minimum values above 2°C during the period between 1979 – 2010. When analysing measurement records of the coldest winters in the Netherlands, available for the period 1907 – 2010 it is noted that the years 1963, 1979, 1985, 1996 and 2010 (for which these last four winters are part of the analysed CFSR dataset) are identified as the coldest winters. It is known from visual observations that during the winter of 1963 the seawater was also not frozen and although floating ice was observed, this was expected to originate from inshore waters floating in offshore direction. Furthermore, it is noted that the surface water temperature increased in the North Sea since 1970 in the order of 0.5-1.0°C and the seawater temperature near the bottom increased in the North Sea 1~6°C during the last 25 years.
115 | General | Certification Bodies | Pre-approved list | Is there a list of pre-approved Certification Bodies that are available to work in the Netherlands? If so, is there any chance you could provide it? | 2016-08-08 | There is no list of pre-approved certification bodies. The certification body must be independent. It is industry standard to use a certification body accredited by a European national accreditation body. Certification by a non-accredited body will not be accepted.
114 | General | Soil Investigation | CPT's in GEF format | With regards to the upcoming tender for Borssele III and IV: Included in the information provided by RVO is soil investigation information as provided by Fugro. The Fugro soil investigation reports comprise CPTs in PDF-format. We would like to receive the CPTs in the so-called GEF-format (Geotechnical Exchange Format), which enables us to efficiently process the soil investigation information. These GEF-format files can be provided by Fugro. Could RVO acquire these files from Fugro? | 2016-07-25 | We interpreted that you do not have access to digital data as it is mentioned that “The Fugro soil investigation reports comprise CPTs in PDF-format”, whereas CPT data has also been issued to RVO in the form of AGS 4.0 and ASCII data.GEF and AGS files contain in principle the same measured data, AGS also contains derived parameters besides measured data only. AGS is an industry-accepted standard format which is internationally used by contractors in the geotechnical field. We advise you on the use of AGS and ASCII files for processing of CPT data.
113 | General | Site Decisions I & II | Appeals against the Site Decisions | If there are appeals against the Site Decisions I and II, will those appeals be made public? If yes, when will they be made public and on which website will this be? | 2016-06-20 | There have been no appeals filed against the Borssele Wind Farm Site Decisions I – V (But they would not have been made public).
112 | General | Dredging | Regulations for dredging | Referring to the cable pre-sweeping activities for IAC dredging might be required. Are there regulations regarding the disposal of dredged material at sea for Borssele I & II (location of disposal areas, dumping fees)? | 2016-04-21 | There is neither a notification requirement nor an additional permit needed for this type of dredging.
111 | Studies | Geological Ground Models WFS III & IV | kingdom project files 'X Y Line Trace Depth Attribute Data' | Is it possible to get the kingdom project files 'X Y Line Trace Depth Attribute Data' for all the interpreted units from the Geological Ground Models for WFS III and WFS IV? These were published on the webpage for WFS I and WFS II. | 2016-04-21 | The complete combined Kingdom Project for Borssele WFS I,II,III,IV and V is available on HDD. This HDD can be ordered by sending an email to: woz@rvo.nl stating the number of HDD's you wish to order and your company's name, delivery address, postal code, city and country. The charge for administrative costs is € 200 per HDD. Please do also state the name, email address and phone number of a contact person, so we can check if everything was delivered according to planning.
110 | General | Boundaries Site 2 | 12-Nautical miles area | Can you confirm the position and shape of Site 2 in relation to the 12-Nautical mile area? According to the available information, the Borssele offshore zone should be located outside the 12-Nautical mile area. In the GIS data however, the 12-Nautical mile area crosses the boundaries of Site 2. What boundary should be taken for Site 2 with regard to wind turbine positions and overhang, 12nm or the Site 2 border? | 2016-04-21 | The boundaries in the Wind Farm Site Decisions are binding.
109 | General | GIS package | Inconsistencies in the GIS package | A few coordinates as given in the Wind Farm Site Decisions show some minor discrepancies with the GIS package on your website. Can you clarify this? | 2016-04-21 | The boundaries of the Wind Farm Sites as published in the Wind Farm Site Decisions are binding. In the Wind Farm Site Decisions two coordinate systems are used. This might show minor differences for some coordinates. These differences can be ignored. The use of both coordinate systems is allowed. One of the requirements in the Wind Farm Site Decisions is that the rotor blades must remain completely within the contours of the Wind Farm Site border coordinates (WFSD I and II, III 2.4). This is the case if the rotor blades remain within the border resulting from one of the coordinate systems
108 | General | TenneT platforms | Coordinates of the platforms | The coordinates of the TenneT platforms are not included in the Wind Farm Site Decisions. They are presented in the memo, but this is not legally binding. What are the official coordinates? | 2016-04-15 | The coordinates can be found in the draft decisions for the permits for the offshore grid (including the substations). These draft decisions can be found at the website of Bureau Energieprojecten: http://www.rvo.nl/subsidies-regelingen/bureau-energieprojecten/hoogspanning/noz-borssele/fase-1. Location of the substations can be found under the requirements "(Voorschrift 1) of (Ontwerp) Watervergunning voor het installeren, gebruiken en opruimen van het net op zee - Borssele van TenneT TSO B.V.": https://www.rvo.nl/sites/default/files/2016/03/OB02_Watervergunning_RWS.pdf
107 | General | Wind Farm Site Boundaries | Distance to boundaries | The Wind Farm Site Boundaries are not always exactly 500 metres from a cable, does this have any impact? | 2016-04-15 | The boundaries of the Wind Farm Sites as published in the Wind Farm Site Decisions are binding. For telecom cables a maintenance zone of 1,000 metres applies. In some cases the telecom cables and pipelines are not exactly in the middle of this maintenance zone due to small bends.
106 | General | Cable crossing agreements | Draft agreements | It is understood that RVO and/or RWS is currently coordinating the preparation of draft standard cable crossing agreements to facilitate private negotiations. Can it be confirmed when the draft agreements will become available? Will the draft agreements include any liability caps? Can an indication of expected liabilities be confirmed? | 2016-03-17 | EZ and RVO are currently investigating the possibility to provide draft crossing- and proximity agreements. More details will follow.
105 | General | Water Decree; transformer station | Certification of transformer station | We are confused about the certification of the substation as mentioned in the below 2 articles of the Water Decree, since the transformer station does not fall within the wind farm operator’s scope. With reference to Decree 153 of 13 April 2015 amending the Water Decree:- Explanatory Memorandum Chapter 6. “Consultation”, section 4: “The Decree has been adjusted to reflect clearly the fact that a certificate from an independent expert relates to all systems that are part of the wind farm, i.e. including the operator´s transformer station”. And: Explanatory Text reg. Article 6.16d: “Pursuant to paragraph 1c), operators must submit a certificate from an independent expert about the design of the wind turbines. This may be e.g. a certificate for the design of the wind turbines and transformer station, including mast construction and foundation. The certificate must document that the design of the turbines and transformer station meets the requirements which Article 6.16g(1) imposes on the technical integrity of the wind turbines and other systems.”The operator is defined as the “natural person or legal entity who establishes or operates a wind farm”. As the transformer station is within the scope of TenneT the design, manufacturing and installation of the transformer is therefore not within the scope of the wind farm operator.This leads us to ask the following questions: Please explain if you still require the operator to submit design certificates covering the Transformer station? If yes, please explain how you think this could be done? | 2016-03-17 | Developers and operators of future wind farms are not responsible for the (TenneT) platforms (transformer stations). The text referred to applies to existing wind farms only.
104 | Studies | Memo and GIS files | Coordinates | We would like to ask you one more item related to the new memo & GIS file. In section ‘1.3 GIS Information’ is written “All coordinates given in this document correspond to GIS data that is made available by RVO through the MPK file of the BWFZ [1].” Does that mean that the coordinates in the memo and the GIS file are interchangeable? | 2016-03-17 | The coordinates in the memo have been extracted from the GIS (.MPK) file.
103 | Studies | Geotechnical deliverables BWFS III & IV | Lacking data | We have noticed that there is some data lacking in the technical deliverable from Fugro. The AGS4 deliverable for the Laboratory testing is incomplete, with one of the groups related to the Particle Size distribution, GRAT, totally absent. The plotting of any PSDs needs this group along with its parent group, GRAG. Is it possible to have this deliverable reviewed by Fugro to allow for a proper transfer of the Particle size data? | 2016-03-17 | Information provided by the GRAG group in the AGS 4.0 files includes data points presented on the geotechnical log, i.e. percentages gravel, sand, silt, clay and fines. The scope of work for this project does not dictate laboratory data AGS files to include individual sieve openings and percentages passing, hence no data is presented for the GRAT group.
102 | General | Modified answer to previously asked (10-12-2015) question: UXO removal by contractor | Modified answer to previously asked (10-12-2015) question: UXO removal by contractor | If UXO removal is done by a contractor, rather than the Navy, will RVO reimburse the costs for this work? | 2016-03-03 | Modified answer to previously asked (10-12-2015) question: A developer is not allowed to undertake UXO removal with a qualified contractor. The Royal Netherlands Navy is responsible for the disposal (removal) of all UXO encountered. Rijkswaterstaat Zee en Delta, part of the Ministry of Infrastructure and the environment, is the competent authority regarding the public security. It is advisable to consult the competent authorities in regards to management measures that can be taken to prevent stagnation in the execution phase. A possible measure is to safely move the UXO outside the work area awaiting destruction.
101 | General | Modified answer to previously asked (10-12-2015) question: Costs of removal UXO | Modified answer to previously asked (10-12-2015) question: Costs of removal UXO | If due to migration, an UXO was identified in proximity to WTG substructures in x years time and was considered a risk (e.g. for maintenance vessels) will the authorities cover the costs of this removal? | 2016-03-03 | Modified answer to previously asked (10-12-2015) question: That is confirmed.
100 | General | Modified answer to previously asked (10-12-2015) question: UXO Removal | Modified answer to previously asked (10-12-2015) question: UXO Removal | Is there any reason why a developer could not undertake UXO removal without involving the Navy, if a suitably qualified contractor was used? | 2016-03-03 | Modified answer to previously asked (10-12-2015) question: A developer is not allowed to undertake UXO removal with a qualified contractor. The Royal Netherlands Navy is responsible for the disposal (removal) of all UXO encountered. Rijkswaterstaat Zee en Delta, part of the Ministry of Infrastructure and the environment, is the competent authority regarding the public security. It is advisable to consult the competent authorities in regards to management measures that can be taken to prevent stagnation in the execution phase. A possible measure is to safely move the UXO outside the work area awaiting destruction.
99 | Studies | GIS | Inter array zones | On the newest pdf map on the rvo.nl webpage, http://offshorewind.rvo.nl/file/download/41267272 there is no mention of an inter array zone. In the newest mpk GIS file; http://offshorewind.rvo.nl/file/view/41082362/base-map-borssele-wind-farm-zone-wfs-i-ii-iii-iv-v-mpk-file-02-12-2015 the inter array zone exists, although it is not a part of the legend in the mpk file. It leaves us with the unanswered question whether the inter array zone is valid or ended up in the MPK file by mistake? | 2016-03-02 | On 2016-02-26 a new memo and GIS file was published, including the inter array zones.
98 | Studies | Geophysical data | Unknown linear target | In the available geophysical data we have noticed an unknown linear target found with a magnetometer. Could you please provide details on the nature of this unknown linear target? | 2016-03-02 | Most likely this is cable KB0081. It is an old, out of use cable. The owner is unlikely to be traceable. Hence no further details are available. The metadata mutation date is 01-07-2015 because this cable is added to the Rijkswaterstaat database as a result of the Borssele Geophysical survey (based on the magnetometer data).
97 | Studies | Floating Lidar | Data | I’ve tried to download Floating LiDAR data and I’ve realized is only available until 14/08/2015. Could you please inform what is going on with the floating lidar and why the data period has not been updated? When is data period going to be updated? | 2016-03-02 | Both buoys have experienced unplanned service needs on shore. Redeployment of both buoys is foreseen in February 2016. The service needs are mainly the effect of unsatisfactory marinisation of the Lidar. In cooperation with the Lidar supplier these problems are now expected to be solved. Available data is quality approved by ECN and published at https://www.windopzee.net/. Please check also the revision log on http://offshorewind.rvo.nl for data updates. The data from 14/08/2015 is expected to be published week 9, 2016.
96 | General | Coordinates | Boundaries | The data package for the BWFZ included among others coordinates for the site boundaries, cable and pipeline maintenance zones & parcels. However, according to the coordinates provided in this data package the parcels are falling within the cable & pipeline maintenance zones. Could you please provide us with consistent coordinates? Data consistency up to centimeter level is of utmost importance for our wind park design. | 2016-02-25 | The boundaries of the Wind Farm Sites as (to be) published in the Wind Farm Site Decisions are binding. In some cases the as found data of the telecom cables and pipelines are not exactly in the middle of the 1,000 metres maintenance zone due to small bends. A new memo with coordinates and GIS file has been made available on 25th February 2016. Please note: The exact boundaries of BWFS will be published in the final Wind Farm Site Decisions. The memo is an update of the boundaries published previously in the draft Wind Farm Site Decisions and will be used as input for the final Wind Farm Site Decisions. Please note that only the boundaries in the final Wind Farm Site Decisions are legally binding. The memo and GIS file confers no rights and is provided for convenience purpose only.
95 | General | Requirements | Trenching | My question relates to the Borssele Offshore wind requirements. Can you please confirm that trenching of in-field cables are not required. | 2016-02-25 | There are no requirements for the burial of in-field cables in the Wind Farm Decisions. Trenching is not mandatory.
94 | General | PSD | Applicable Law | Regulation 5 Monitoring and evaluation programme from Borssele I & II Appendix B ‘Applicable Law for Offshore Wind Energy’ states that: d) The Minister of Economic Affairs will create an environmental monitoring and evaluation programme. The permit holder will collaborate as far as possible, without financial compensation, in this monitoring and evaluation programme. The footnote to this states ‘The aim of this programme is set out in Appendix 1 of this decision’. Can you please clarify where I can find Appendix 1 with these details? By ‘decision’, does it mean the sign off for the projects to go ahead which is currently delayed? Are there any projected costs for assisting in the monitoring – is the developer just responsible for allowing monitoring to take place, or does the developer also have to fund additional monitoring schemes? | 2016-02-25 | ‘Decision’ refers to the Wind Farm Site Decision. The reference to “Appendix I of this decision” is not correct. The reference should be "The aim of the monitoring programme is set out in section II of the (draft) Wind Farm Site Decision (available in Dutch only)". Collaboration with the Ministry of Economic Affairs is mandatory and restricted to allowing monitoring to take place and assist herein. The developer will not be compensated for the costs of this collaboration and assistance. The developer does not have to fund additional monitoring schemes.
93 | Studies | Morphodynamics | Update Morphodynamics report | We would like to see the Borssele morphology report. You state on the webpage that it has been updated in Q4 2015 but when we go to the mophodynamical desk study for Borssele I&II the report dates to 24 February 2015 at 10:39 am. How can we access the updated version of this report; can it be emailed or will you update the link to show the most recent version? | 2016-02-25 | The update announced for Q4 2015 is the update for BWFS III, IV and V. This report has been published in January 2016.
92 | General | Regulation 2 Wind farm and design specifications | Repair and maintenance | Regulation 2 Wind farm and design specifications, 17: During repairs and maintenance of telecommunication cables the number of rotations per minute per wind turbine of the wind turbines that are present within a radius of 1,000 metres of the repair and maintenance location must be reduced to less than 1. Are there any values available for how often these may need maintenance and how long that takes? Does this also include routine inspections? Is there any compensation mechanism for not producing electricity during these periods? | 2016-02-25 | This has to be concluded in crossing and/or proximity agreements between the wind farm owner and the cable or pipeline owner(s). Crossing and proximity agreements fall under private law, hence formally we cannot answer your questions. Practical experience teaches us the following: In the past 10 years hardly any repairs were needed on the telecom cables in the BWFZ. Moreover, there are no repeaters (relatively high-maintenance devices) in the telecom cables in the BWFZ. For the future situation: Any disturbing of the seabed (like trawl fishing) will not be allowed in the entire Wind Farm Zone except for the shipping lane, hence the probability that repairs are necessary is (very) small. Routine inspections and planned maintenance will be done in the maintenance zones only, frequency is estimated at ~ every 4 years. In the (unlikely) event that a cable needs to be repaired, the wind farm owner can contact the cable owner to get their costs reimbursed from the liable party.
91 | General | Certification | Project certification body | Will there be a project certification body or comparable entity involved over the lifetime of the project, by some sort of periodic inspections? | 2016-02-23 | This is not foreseen.
90 | General | Requirements | Operational modifications | In Germany, new wind farms are required to modify operations of those turbines whose wake effect would exceed the assumptions used in designing previous installed wind farm(s). These operational modifications typically occur only during periods of high wind speeds, and typically only need apply to the one or two rows of turbines immediately adjacent to the previous installed wind farm. Does the Netherlands have now, or does it plan to have, a similar requirement as in Germany, in which new wind farms must modify their operations as needed in order to ensure the structural stability of existing wind farms? | 2016-02-23 | There are currently no similar requirements foreseen.
89 | General | Standards and guidelines | Standards and guidelines | Which standards, recommendations, guidelines, obligations are to be followed for design, manufacturing, installation, commissioning and operation of the WTG, Foundation, Cable, interfaces? | 2016-02-23 | Internationally recognised standards. It is not possible to present a complete overview.
88 | General | Water Decree | Ministerial Order | Article 6.16g (4) of the Water Decree says "A ministerial order may lay down rules on the content of a declaration referred to in the second paragraph." Does such ministerial order, or a draft or a term-sheet, already exist? | 2016-02-23 | No, it does not. A brief guideline will be drafted that outlines which data in the various plans has to be submitted.
87 | General | PSD | Electrical Infrastructure | The PSD BWFS I and II V2, august 2015, Section 6.2.6 “Electrical Infrastructure” mentions: -six 66 kV bays for the inter-array cables per PPM, resulting in four bays "one string – one bay" and two bays "two strings – one bay" on the offshore substation; and - 18 J-tubes for the inter array cables: 2x 8 J-tubes for offshore PPM; 1 J-tube installed for possible test purposes; 1 J-tube installed for the connection to the neighboring platform. It is assumed that the test J-tube and the one for the neighboring platform cannot be utilized for the inter-array cables. If so, why are the J-tubes for the export cables not listed? | 2016-02-23 | n the published draft scenario offshore wind energy dated 16-12-2015 (will be renamed to ‘development framework for the offshore grid’); a number of 2 J-tubes is listed for the 220 kV export cables.
86 | Studies | Archaeology | Exclusion zone | Are you able to inform about the size of the exclusion zone around a potential object of archaeological value? | 2016-02-22 | In general a buffer or safety zone of 100 metres around an archaeological object or an object with an archaeological expectation is to be defined, in which no activities such as trenching or anchoring are allowed. If additional research shows that the object has no archaeological value, the location and the buffer zone can be omitted.
85 | General | Environmental Impact Analysis | Summary Environmental Impact Analysis | You have provided ‘Summary Environmental Impact Analysis’ for Borssele wind farm sites I & II. Where can we find the information and reports used for the EIA? | 2016-02-22 | The Environmental Impact Analysis and related documents are available in Dutch only and can be downloaded: www.rvo.nl/subsidies-regelingen/wind-op-zee-kavels-borssele
84 | Studies | Seabed mobility | Time-series | When will the time-series of seabed mobility be available again? | 2016-02-22 | The updated morphodynamic report for BWFS IV, III and V have been published.
83 | Studies | Metocean report | Sea/swell components | Is it possible to add a partition of sea/swell components in the Metocean report? That is important to assess fatigue. And is it possible to deliver Directional Normal Sea State (NSS) tables for every Hs-Tp-Vel.wind combination (now, Hs-Tp for time series is omnidirectional)? | 2016-02-22 | We do not intend to add this information. This would extend the scope of the current Metocean desk study substantially and the information probably would come not in time for the first and the second subsidy and permit tender. We will consider to include this in the scope for Wind Farm Zone Hollandse Kust.
82 | Studies | Floating lidar | pre-deployment validation report | With reference to the floating lidar / supply of meteorological and oceanographic data reports at Borssele Wind Farm Zone (BWFZ), I have been able to find the following reports until now; Monthly Progress Report: 14 July – 14 August 2015, Reference No: C75339_MPR01_R3 (20 Nov. 2015) Validation report: 14 July – 14 August 2015, Reference No: C75339_VAL01_R2 (20 Nov. 2015) Monthly Progress Report : 14 July – 14 August 2015, Reference No: C75339_MPR02_R4 (20 Nov. 2015) Validation report: 14 July – 14 August 2015, Reference No: C75339_VAL02_R4 (20 Nov. 2015) According to the documentation the buoy was first deployed on 11th June 2015. We would normally expect that a validation study in the immediate vicinity of an offshore met mast to be completed before the installation. Could you please provide us with the pre-deployment validation report, if available? | 2016-01-21 | This predeployment validation report can be found at; http://offshorewind.rvo.nl/file/view/41053352/public-predeployment-validation-report-buoy-1
81 | Studies | Grid data | Geophys .dat files BWFS III | For a 3D-GIS-Project I tried to download the grid-data for the wind-farm Borssele III and IV. The grid-data-folder in http://offshorewind.rvo.nl/file/owner/WOZ_RVO.nl#39047072 is empty. Is it possible to get the grid-data for the geological units? | 2016-01-21 | The requested grid data on the geological charts (appendix N) of BWFS III and IV could not be uploaded due to technical problems. These problems are solved and you can find the grid data here. All geophysical site investigations data (including the .dat files) on BWFS III, IV and V is available on hard disk. You can order the hard disk here: http://offshorewind.rvo.nl/file/download/40117062
80 | General | Certification | Norms and standards for certification | We would like to know if there is a preference in the use of norms and standards for certification in the Borssele project and if so, which is the hierarchy when using them. We are also interested in knowing which certification bodies will be accepted in the Netherlands or whether we can make use of external companies if these are accepted. Is it possible to use Eurocode as the main standard for design or are other offshore specific standards such as DNV, GL and IEC preferred? | 2015-12-10 | Eurocodes can be applied if they concern offshore windturbines. All international accepted norms and standards can be used. For detailed information we refer to the draft SDE+ and permit application form, page 13, appendix 11, see here. The certification body must be independent. It is industry standard to use a certification body accredited by a European national accreditation body. Certification by a non-accredited body will not be accepted.
79 | Studies | WRA | Additional information Wind Resource Assessment | In order to perform a meaningful yield and turbulence study please provide the measured wind distribution as a matter of wind direction as table and the turbulence level (average and standard deviation) as a matter of windspeed. Is this something that can be provided? It was partly contained in the ECN quick scan from June 2014. | 2015-12-10 | Today we have published this additional information. You can find it here.
78 | General | Bird migration | Bird migration | Please confirm the timespan of monitoring that is required to determine if bird migration requires turbine slow-down. a. Should monitoring be done continuously throughout each 24h period during months of migration, where a 24h period corresponds to a day – e.g. 0500-0459? b. If the threshold for migration is reached in only 1 hour of any day/24h period, does this qualify to implement the slow-down condition or is appropriate to say “where the threshold is met for at least x hours in any 24h period (i.e. 0500 – 0459), this will require slow-down conditions to be instigated? c. If the threshold is not reached during day light hours but is met during the hours of darkness, is slow-down required for the remaining hours of darkness during that 24h period (as defined in a)? d. What are the months you define as relevant to bird migration activity? | 2015-12-10 | More detailed information is not yet available.
77 | General | Water Decree | Cables burial depth | Are there any requirements for inter array cables burial depth? The Water Decree only specifies this for Export cables to be 1.0 meter. Would the developer for instance be allowed, if preferable from a risk perspective, not to bury the cables? | 2015-12-10 | There are no requirements for the burial depth of inter array cables.
76 | General | Private agreements | Private agreements required? | With the exception of cable crossings, are any other private agreements required with regards to the offshore wind farm? | 2015-12-10 | That is up to the developer.
75 | General | Existing cables | Proximity to existing cables | Please confirm, are private agreements for proximity to existing cables required under Dutch law or are the site decision conditions sufficient? | 2015-12-10 | The Wind farm Site Decisions do not determine crossing and proximity conditions. Crossing and proximity agreements with cable and pipe line owners fall under private law.
74 | General | European Species Licence | European Species Licence | Will a European Species Licence be required for any impact piling work or does the Kavelbesluiten cover any such requirement determined by the Habitats Directive? | 2015-12-10 | The Wind Farm Site Decision covers all requirements. No other permits / consents are needed.
73 | General | Water Decree | Next version Water Decree? | What is the timeline for the second version of the Water Decree to come into force? | 2015-12-10 | There is no revision or next version of the Water Decree planned at this moment.
72 | General | Safety Zone | Fishing activities 2 | In the future revision of the Water Decree, will fishing activities affecting the seabed also be banned from OWF safety zones? What about within the wider Borssele zone – e.g. within the shipping channel? | 2015-12-10 | There is no revision or next version of the Water Decree planned at this moment. Any disturbance of the seabed is prohibited. This applies to the whole Wind Farm Zone, including all maintenance zones and the shipping channel.
71 | General | Safety Zone | Fishing activities | Will fishing be banned from TenneT cable corridors and any safety zone around OSPs? | 2015-12-10 | Any disturbance of the seabed is prohibited.
70 | General | Water Decree | Export cables | Within the Water Decree there are a number of conditions stated for “export cables”. Please can it be confirmed that the term export cable only refers to TenneT cabling and the term does not include inter-array cabling within a wind farm? | 2015-12-10 | Confirmed.
69 | General | Seaway | Shipping passage | Please can it be confirmed if the shipping passage between the Borssele wind farm sites is defined as a “seaway”. If it is, please confirm the maintenance depth of this seaway. | 2015-12-10 | The shipping passage is not a seaway.
68 | General | UXO | Costs removal UXO not by Navy | If UXO removal is done by a contractor, rather than the Navy, will RVO reimburse the costs for this work? | 2015-12-10 | If UXO removal is done by a contractor, costs will not be reimbursed.
67 | General | UXO | Removal UXO not by Navy | Is there any reason why a developer could not undertake UXO removal without involving the Navy, if a suitably qualified contractor was used? | 2015-12-10 | A developer is allowed to undertake UXO removal with a qualified contractor.
66 | General | UXO | Removal UXO | If due to migration, an UXO was identified in proximity to WTG substructures in x years time and was considered a risk (e.g. for maintenance vessels) will the authorities cover the costs of this removal? | 2015-12-10 | Confirmed.
65 | General | Vessels | Size vessels | For Borssele I & II there is a statement that vessels no larger than 45 meters can transit through the west-east shipping land and vessels no larger than 24 meters can pass through the wind farms. Is that vessel size only during operation and for non-wind farm vessels (can our O&M and construction vessels exceed this)? | 2015-12-10 | This applies to non-wind farm vessels only. There are no restrictions for the developer for (construction and O&M) vessels. During construction only wind farm vessels are allowed to pass through the wind farm.
64 | General | Information Belgian wind farms | MUMM | Where can I find information about the Belgian wind farms? | 2015-12-10 | MUMM recently updated their website. The new link to the MUMM information about the Belgian wind farms is: http://www.mumm.ac.be/EN/Management/Sea-based/windmills.php
63 | Studies | UXO | Statement UXO's | Is the statement on UXO's in the Project and Site Description only, or is it backed by formal legislation or other formal documents related to the Borssele tender? | 2015-12-09 | This statement in the PSD is the applicable procedure.
62 | Studies | Additional soil information | Thermal resistivity | To enable the design of the Inter Array Cables cross sections we would strongly require additional soil information. Having this information will enable developers to prepare a lower bid price with less contingency/risks included. The Fugro geotechnical reports do not include this information. The parameters concerned are the sea bed temperature (in °C), and the sea bed thermal resistivity (in K.m/W). We would appreciate the information to be made available on shortest possible notice. | 2015-12-09 | At the moment we are checking if the thermal resistivity can be made available.
61 | General | Archaeological findings | Exclusion zone | With reference to the PSD (section 4.3) could you please inform if there is an exclusion zone to be respected during construction around identified historic shipwrecks or other potential archaeological findings within the wind farm area? | 2015-12-09 | In the final Wind Farm Site Decisions a requirement will be added to protect objects with an archaeological value. For objects which cannot be avoided during construction the archaeological value has to be investigated. If an object with archaeological value is found, it has to be protected; this includes an exclusion zone. In the archaeological desk study it is concluded that the chance to encounter prehistoric archaeology within the wind farm zone is small (=low sensitivity). The chance to encounter historic archaeology (shipwrecks, airplanes etc) is average (=medium sensitivity).
60 | Studies | Base Maps | Base Maps in MPK files | The update "Progress update Roadmap towards 4.500 MW offshore wind energy", sent December 2nd, contains a link to altered Base Maps Borssele I - V. However, this information is in .MPK format, which we cannot access. Will this data also be available in other formats, e.g. pdf? | 2015-12-09 | Yes, a pdf version is now available, on the page 'Maps Borssele'.
59 | General | Bligh Bank | Maintenance zone Bligh Bank | With reference to the Q&A published 27-11-2015 regarding "Safety zone Bligh Bank" could you please inform the size of the maintenance zone for the cables from Belwind and Northwind? Further, could you please make the as-built coordinates for the export cables available? | 2015-12-09 | For information about the Belgium wind farms we refer to the Belgium authorities: http://www.mumm.ac.be/EN/Management/Seabased/windmills.php
58 | Studies | UXO | Contact details navy | What are the contact details of the navy regarding UXO issues? | 2015-12-09 | Dutch Coast Guard: https://www.kustwacht.nl/en/contact.html
57 | Studies | UXO | UXO Removal Procedure | Reference is made to the Project and Site Description document section 4.4.5 UXO removal procedure and the following text: "if a wind farm developer identifies an UXO on a location where a foundation of a wind turbine is planned, it should be reported to the Dutch Coastguard. The Dutch Navy will remove the UXO and detonate it on a safe location. No costs will be charged to the wind farm developer." Will the guaranteed removal at no costs for the developer also be applicable to removal of UXO's for the planned Inter Array cable routes if any UXO are identified on these routes? | 2015-12-09 | That is confirmed.
56 | Studies | Geo-hazards | Geo-hazards on the seabed | Is it possible to provide specific detailed information on geo-hazards on the seabed so as to confirm/discard its presence at Borssele? | 2015-12-09 | Detailed information about geo-hazards is to be found in the deliverables of the geophysical site investigations.
55 | Studies | UXO | Extensive UXO Study scheduled? | There is an UXO desk study with scarce information. This is especially sensitive around wrecks, as the identification of magnetic objects can be troublesome since the wrecks hold a lot of magnetic material by themselves. More magnetic objects will most likely be found, if a survey with closer line spacing is performed. It must also be addressed that objects will be buried and emerge on seabed by the dynamic seabed movements. Evaluation of possible burial depth of UXO is missing. Question: is a more extensive and complete UXO study scheduled? | 2015-12-09 | There is no other UXO study scheduled. In the UXO desk study it was adviced to undertake a detailed UXO survey close to the start of construction. A detailed study at this stage would not have an added value due to the dynamic behaviour of the Wind Farm Zone.
54 | Studies | LiDAR Data | Availability data | I am trying to retrieve Lidar Data from the floating lidar at the Borssele Center. As described on the website, I only ask (statistical) data per month. Is it correct that for now only data from 15-06-2015 until 14-08-2015 is available? If yes, when can we expect more data become available? | 2015-12-01 | Yes, it is correct that at November 27th two monthly periods have been published. Please note that these are updates of the wind direction data of the first two periods, due to a correction of this data. Data for period three is (after quality assurance and quality check) scheduled for publication in week 51.
53 | General | Safety zone | Bligh Bank | Has a safety zone of 750 meters been considered for the export cable of Bligh Bank? This export cable connects the Bligh Bank OWF to the onshore substation in Zeebrugge. This cable runs in parallel with the SW border of Borssele. If the standard 750 meters safety zone is applied to this cable, the resulting safety zone still overlaps with the designated net areas of Borssele (kavel IV, III and II). Has this cable and its safety zone been considered in the definition of the Borssele net areas or not? | 2015-11-27 | We assume this refers to the export cables from Belwind and Northwind between these wind farms and the Belgian - Dutch border. This does not effect the boundaries of the wind farm sites. However, when the Borssele wind farms II, III and IV are built a safety zone of 500 meters will be established around the wind farms. These safety zones overlap with the maintenance zone of the Belgian export cables. The Belgian wind farm owners will get permission to enter these safety zones for maintenance and repair operations and will have to conclude a proximitee agreement(s) with the owners of wind farms II, III and IV.
52 | General | Bird collisions | Bird monitoring equipment | With reference to the mitigation measures to reduce bird collisions following from the Draft Site Decisions could you please answer the following: Can you confirm that the offshore wind farm developer can place bird monitoring equipment (radar) on the offshore substation? If confirmed, please clarify any technical limitations to such equipment (e.g. no of radars, position and placement etc.)? | 2015-11-27 | TenneT and the authorities are working on a plan for this kind of monitoring equipment to be installed on the platforms. Ideally these would be shared services and realized in cooperation between the wind farm owners, TenneT and the authorities.
51 | General | Bird collisions | Shut-down during bird migration | With reference to the mitigation measures to reduce bird collisions following from the Draft Site Decisions could you please answer the following: As regards the required shut-down (to < 1 rotation per minute) of wind turbines during nights with large-scale bird migration please clarify if the offshore wind farm developer should comply with a certain shut-down sequence as e.g. “xx MW per minute” or “complete shut-down in xx minutes” of the entire wind farm - plot I and II respectively? | 2015-11-27 | The start - stop procedure is not pre-defined and must be part of the execution plan that has to be submitted to the authorities at least 8 weeks prior to the start of the construction (Companies are advised to submit a draft execution plan at a much earlier stage).
50 | General | Wind Farm Site Decisions | Sound level during piling work | If we want to build a wind farm with 80 wind turbines, how should we interpret the table with the limits for sound level during piling work (WFSD – III regulations – Regulation 4.2)? Is that: A) can we install up to 76 wind turbines in the period January – May with a sound level not exceeding 160 dB and the remaining 4 wind turbines in the period June – August with a sound level not exceeding 171 dB, or B) is piling work prohibited in the period January – May, and construction must take place in the period June – December? | 2015-10-27 | The correct interpretation is option –B-. If a wind farm consists of 77 or more wind turbines, piling work is prohibited in the period January – May.
49 | Maps | GIS data | MPK file | When going through the latest GIS data published on the rvo.nl webpage, we have encountered an apparent mistake in the 'SDB_20150720_RVO_FN_shipping_corridor' feature from the 13/08/2015 GIS data update: http://offshorewind.rvo.nl/file/view/33717532/base-map-borssele-wfz-mpk-file. It appears from the attribute table content (see attached copy) that a potential cable exclusion zone may have been published under the name 'SDB_20150720_RVO_FN_shipping_corridor'? Could you please clarify whether this is intentional or a potential mistake in naming of attributes/files? | 2015-10-19 | In the attribute table some orphans have been found. This mistake is corrected, a new version of the MPK file has been uploaded. This does not affect the boundaries or coordinates.
48 | Maps | Differences between coordinates |  | There are small differences between the coordinates in the draft Wind farm Site Decisions & the online GIS model. What coordinates are leading and will these be matched in future? | 2015-10-13 | The coordinates in the (final) Wind Farm Site Decisions will be leading. Small differences cannot be avoided, this is related to the chosen number of decimals and the resulting rounding off. In practice differences will not be higher than approx. 5 millimeter.
47 | Studies | Update floating LiDAR measurement campaign |  | Could you provide an update on the floating LiDAR measurement campaign, like installation date and photos, start of measurements, when and how the first data will become available? | 2015-10-13 | Reports will be published on this website. Data can be found on www.windopzee.net.
46 | Studies | Metocean study | Peak enhancement factor of the JONSWAP spectrum | The peak enhancement factor of the JONSWAP spectrum is given as 1.44 for all NSS in Table 4.5 of the metocean report. This is in contradiction to the report text where it is claimed that the peak enhancement factor is determined by the Torsethaugen et al. (1984) method, and furthermore, in section 4.6 of the metocean report it is claimed that a JONSWAP spectrum with peak enhancement factor of about 1.134 is expected to characterize the sea states in the Borssele zone. Please could you clarify which gamma is correct and provide some explanation as to why that value is most appropriate? | 2015-10-12 | This is a typo/inconsistency in the report. None of the printed peak enhancement factors of the JONSWAP spectrum (gamma) is correct. It is recommended to use a gamma value of 2 in general in the BWFZ region given that this estimate (based on the measured Tp / Tm-1,0 ratio) is in our opinion more robust. This value has also been applied in the numerical wave modelling (boundary conditions of SWAN).
45 | Studies | Geotechnical Investigations | GIS data | We noted that the deliverable for the geotechnical investigations for WFS I and II “X Y Line Trace Depth Attribute Data - Fugro Borssele” are identical for both WFS I and WFS II. Is this correct? | 2015-09-30 | This is correct. “X Y Line Trace Depth Attribute Data - Fugro Borssele” contains the data for WFS I and II, therefore the same file has been published twice.
44 | Studies | Wind Resource Assessment | Wind speeds | We think the wind speeds in the Ecofys wind resource assessment are too high. Can you: 1) hire a third party who can make an assessment taking into account the latest available wind data i.e. including the data from LE Goeree and the Metocean data; 2) Issue a statement of compliance, which will improve the bankability of the project for investors. | 2015-09-30 | This is a preliminary wind resource assessment. RVO.nl decided not to create other assessments before Q2 2016. Tender applicants are advised to create their own assessment(s). We have asked DNVGL to issue a Statement of Compliance (SoC). The updated report and the SoC have been published September 2015.
43 | General | TenneT export cable | Coordinates | Could you possibly make the coordinates for the selected trajectory for the TenneT export cable available on the RVO web? | 2015-09-15 | The exact route of the export cables is not yet known. TenneT expects to submit the permit applications by the end of 2016. The draft permits will be published at the beginning of 2016. By then the coordinates will be known.
42 | General | PSD | Editable version | Would it be possible to receive a word/editable version of the PSD, specifically of 'Section 6 Specific requirements and relevant information from the legal framework'? | 2015-09-14 | We have provided a translation of the requirements relevant for this stage of development for your convenience. We do not provide editable versions for QC reasons.
41 | General | Soil samples | Future use soil samples | Will the soil samples from the geotechnical boreholes at the Borssele site be stored for future use? If so, for how long? | 2015-08-28 | The remaining samples will be stored until the winners of the tenders are known, and handed over to them.
40 | General | Turbine design parameters |  | Previous question: What are the turbine design parameters (design envelope) above sea level height requirements measured in: MSL, LAT or MHWS? RVO answered on 26-05-2015: "In the wind farm site decision the maximum height of the rotor blades, the minimal distance between LAT and the lowest point of the rotor blades and the distance between the individual WTG towers will be defined". However, according to the draft Site Decision recently published for consultation it follows from "Requirement 2 Wind farm and Bandwidths" the above dimensions are measured in MSL. Could you please clarify? | 2015-08-28 | In contradiction to the answer dated 26.05.2015 in the draft wind farm site decisions dimensions are measured in MSL.
39 | General | Foundations | Gravity based foundations | Are gravity based foundations (GBF) allowed and what are the related requirements for underwater noise mitigations, i.e. the maximum foundations to be installed per year? | 2015-08-28 | Gravity based foundations are allowed. Underwater noise is not at issue. The maximum number of foundations is linked to the allowed maximum number of turbines.
038 | Studies | Safety zone around site boarder | Definition of safety zone | A 500 meter safety zone is described and sketched in Section 3.5 in the latest and final version of the Site Studies Wind Farm Zone Borssele – boundaries & coordinates wind farm zone. Could you please inform about the definitions of this safety zone and what is allowed within this zone. Is it e.g. allowed to jack up during installation within this zone? | 2015-08-24 | A safety zone of 500 m will be enforced after the first foundation in the wind farm is set. Any installation or overhanging rotor blades or access to a safety zone is prohibited. But the owner of the wind farm is of course allowed to enter the safety zone around his wind farm with (jack up) vessels. In some cases, where a safety zone overlaps a maintenance zone of a pipeline or cable, the owner of that pipeline or cable will be allowed to enter the safety zone for maintenance operations. There are no other limitations in safety zones, jack up operations are allowed.
1 | General | Safety zones and distances | Coordinates helicopter flight path | Could you please make the coordinates for helicopter flight paths (if defined yet)? What is the safety distance rule regarding the rotor diameter? | 2015-07-07 | Platforms Alpha and Beta in the BWFZ will not be equipped with helicopter landing decks. Hence there are no flight paths to consider. The Minister of Economic Affairs will officially confirm this before summer 2015.
2 | Studies | Wind data KNMI | Publication | 1. Will the (raw) wind data that is being used for the wind resource assessment of Ecofys be made public by RVO? 2. Is there a restriction from RVO's side that the (raw) data that KNMI has provided to Ecofys will be published on the site of RVO together with the wind resource assessment made by Ecofys? | 2015-07-07 | 1. KNMI plans to make the dataset available on their website in July (including all information on how to use the dataset) 2. KNMI made an exception for Ecofys to use the HARMONIE data for the wind resource assessment, because the deadline was earlier than July. KNMI and RVO would like to avoid that discrepancies might occur in different versions of the dataset available from different locations, especially considering the fact that a dataset can be updated regularly. Therefore, the basic data will be published by its originator (KNMI in this situation) and RVO publishes the results of the analysis carried out by Ecofys on the KNMI data. See also Q&A 5.
3 | General | Website updates | Notification | Is it possible to subscribe to a news-agent/mailing where one get notified each time the RVO Q&A web is updated? | 2015-07-07 | Updates on the website have to be checked by yourself. On the website you will find a revision log where all revisions are listed. Please note that the URL has changed into offshorewind.rvo.nl
4 | General | Wind Farm layout | Yield optimisation | Can you please confirm that the developer – with respect to project area borders, safety zones, etc. – has full freedom to make a wind farm layout based on yield optimisation; for example a curved layout or with a dense border of turbines (see as an example the Danish Offshore Wind farm Anholt in the figure below) versus a layout where turbines are in straight lines? | 2015-07-07 | Confirmed. There will be no other restrictions to the wind farm lay out other than the general rules and the design envelope. Restrictions to the lay out itself are not foreseen. An updated overview of the restrictions will be included in the 2nd revision of the Project and Site Description. This is planned for publication end of July - beginning of August 2015.
037 | Studies | Wind speed data |  | The wind speeds found by Ecofys (in the wind resource assessment) differ from the wind speeds found by Deltares (in the metocean study). What are the reasons for the differences and does this have consequences for the studies which are already published? | 2015-07-02 | As stated in section 3.4.3 of the Ecofys wind resource assessment, these differences are related to the use of the Harmonie model by KNMI. The adjustments made by KNMI can be read in Section 1.1.3 of Validation of KNW atlas with publicly available mast observations (Phase 3 of KNW project) (www.knmi.nl/bibliotheek/knmipubTR/TR352.pdf). There one can read that “Geertsema (2014) concluded that the model underestimates the vertical wind shear by a factor of about 15% which implies that the wind at a 100 m height is underestimated by about 5%”. The applied correction for wind speed is –depending on the roughness- about -2% (overestimation) at 10 m to +5% (underestimation) at 100 m. Waves and water levels are a function of the drag at the surface and related to the 10-m wind speed. This function is –about- linear to quadratic. This implies that a variation of a% in the wind speed will result in a variation ranging from a% to 2a% in the wave heights and the water levels. Therefore, an overestimation of 2% of the 10-m wind speed means that the waves and water levels are overestimated by at most 4%. Such differences are within the uncertainty ranges given in the Metocean report and the Wind Resource Assessment. Differences between the studies are within uncertainty ranges and can be explained, therefore, there is no need to update the already published Metocean report(s).
5 | Studies | Wind data KNMI | Publication | It has been announced on the website of RVO a 34 year long created time series with wind data for grid points in the Borssele Wind Farm Zone made by KNMI will be made available by RVO.nl. Is this still the case? | 2015-06-23 | KNMI is planning to make this dataset available online in July - August 2015. More information can be found in the following reports: http://www.knmi.nl/bibliotheek/knmipubTR/TR352.pdf http://www.knmi.nl/bibliotheek/knmipubTR/TR353.pdf. See also Q&A 029
6 | Studies | Data availability | LiDAR Light Island Goerée | Is the data from the fixed lidar that is installed at light island Goerée since October 2014 available? | 2015-05-28 | ECN is performing a four year meteorological measurement program on the Dutch part of the North Sea, requested by the Ministry of Economic Affairs. Via the website www.windopzee.net developers can download wind data of meteo station IJmuiden. At the moment it is not possible to download wind data of Light Island Goerée and Europlatform, but it will be in the future. Wind data of Light Island Goerée can be obtained by sending a request via the contact page: https://www.windopzee.net/lichteiland-goeree-leg/contact/.
7 | General | Wind farm layout | helicopter corridors | Are there any requirements for incorporation of designated helicopter corridors within the wind farm to be used for Search and Rescue (SAR) purposes? | 2015-05-26 | Incorporation of designated helicopter corridors within the wind farm to be used for Search and Rescue (SAR) purposes is not foreseen.
8 | General | Safety zone | Project and site description | According to section 4.3 of the “Project & Site Description”, a single width safety zone of 500m has to be taken into account for sand extraction areas. A sand extraction area is located to the south-east of parcel II. The coordinates of the parcels are specified in the memo “Wind Farm Sites and investigation zone around sites” dated 02.12.2014 and authored by Maarten Timmerman. Do the coordinates in the memo already reflect the safety zone of 500m or is it necessary to deduct a strip of 500m from the parcel’s area? | 2015-05-22 | In the concept of wind farm site decision Borssele II (available at http://www.noordzeeloket.nl/images/Concept-ontwerpkavelbesluit%20Borssele%20II%20ten%20behoeve%20van%20consultatie%20in%20mei%202015_4174.pdf) the coordinates of the wind farm site are included. For sand extraction in the concept it is concluded, that the safety zone around the wind farm will mean a little less sand extraction (3%). Previous given answer 6-3-2015: The coordinates in the memo already include all safety zones to be respected.
9 | General | Wind farm layout | Location turbines | Will the Tenderer have full freedom to locate the turbines within the wind farm plot in order to optimize production (i.e. no requirements for turbines in straight lines/ grid based layout)? | 2015-05-22 | The winning tenderer will receive a license which allows him to build and operate a wind farm at the specific site. In the wind farm site decision, the bandwidth of design characteristics will be defined. In the concept of wind farm site decision Borssele II (available at http://www.noordzeeloket.nl/images/Concept-ontwerpkavelbesluit%20Borssele%20II%20ten%20behoeve%20van%20consultatie%20in%20mei%202015_4174.pdf) the draft bandwidth of design characteristics is presented. There are no requirements for turbines in straight lines / grid based layout in this concept of the wind farm site decision.
10 | General | Wind farm layout | Procedure lay out approval | In case of any layout requirements the Tenderer needs to have his layout approved by the competent authority before tender submission in order to submit a firm bid as layout restrictions will impact the business case. What will be the procedure for layout approval during the tender process? | 2015-05-22 | The bandwidth and other restrictions defined in the wind farm site decision must be respected. There is no pre-approval procedure foreseen.
11 | General | Turbine design parameters | requirements | What are the Turbine design parameters (design envelope) above sea level height requirements measured in - MSL, LAT or MHWS? | 2015-05-22 | In the wind farm site decision the maximum height of the rotor blades, the minimal distance between LAT and the lowest point of the rotor blades and the distance between the individual WTG towers will be defined.
12 | General | Offshore substation (OSS) parameters | Minimum distance | Is there a minimum distance from WTG tower to OSS? | 2015-05-22 | Yes, a safety zone of 500m must be respected.
13 | General | Offshore substation (OSS) parameters | Cable free zone | Is there considered a cable free zone of one of the OSS sides and what is the size and position of that zone? | 2015-05-22 | Yes, a cable free zone is foreseen to allow jack-up operations, this will probably be on the East side of the TenneT Alpha platform.
14 | General | Offshore substation (OSS) parameters | Location turbines | Can turbines (the centre of the foundation/turbine tower) be placed on the edge of the wind farm territory and safety zones around cables, pipelines, sunstation etc.; i.e. will it be accepted that the wing tips are "overhanging" boarders and safety zones? | 2015-05-22 | In contradiction to what is presented in the project and site description overhanging will not be allowed. Safety zones must be respected to the blade tips, see article 2 sub 2 (page 53) in the concept of wind farm site decision Borssele II (available at http://www.noordzeeloket.nl/images/Concept-ontwerpkavelbesluit%20Borssele%20II%20ten%20behoeve%20van%20consultatie%20in%20mei%202015_4174.pdf).
15 | General | Safety zones and distances | Coordinates piloting zone | Could you please make the coordinates for the piloting zone in the NE part of plot I available? Are wing tips - as asked above - allowed to be overhanging the area? | 2015-05-22 | This information will soon be available, see tab "maps" of this website. Wing tips won’t be allowed to be overhanging the piloting area.
16 | General | Safety zones and distances | Cable crossings | What are the restrictions for cable crossings - can the crossings be distributed along the cables or should there be a cable crossing corridor? | 2015-05-22 | As shown in article 2 sub 9 (page 53) the concept of wind farm site decision Borssele II (available at http://www.noordzeeloket.nl/images/Concept-ontwerpkavelbesluit%20Borssele%20II%20ten%20behoeve%20van%20consultatie%20in%20mei%202015_4174.pdf), there are restrictions for cable crossings towards platform Borssele Alpha.
17 | General | Safety zones and distances | Jacking up | Is jacking up on and outside the site boundary allowed during installation of WTGs and cables? | 2015-05-22 | No, jacking up outside the boundaries according to article 2 sub 2 (page 53) is prohibited, see concept of wind farm site decision Borssele II (available at http://www.noordzeeloket.nl/images/Concept-ontwerpkavelbesluit%20Borssele%20II%20ten%20behoeve%20van%20consultatie%20in%20mei%202015_4174.pdf)
18 | General | Safety zone | Rembrandt 2 cable | Has a safety zone for the Rembrandt 2 cable been considered within the net area definitions for Borssele? The Rembrandt 2 cable connecting Domburg to Margate (UK) passes Borssele in the SE corner. It seems that no 750m safety buffer to this cable has been applied in the definition of the Borssele net area because it still overlaps with the project boundaries of kavel II . Was this cable and its safety zone considered in the net area definition? | 2015-04-08 | The Rembrandt 2 cable is an out of use cable, hence, the safety zone for this cable is not applicable anymore.
19 | Studies | Metocean study | Persistence tables | Is it possible to obtain outputs from one or more points of the following models: Output from local model on which Deltares generated the persistence table (input data to attachment 1), i.e hourly time series data (bulk and spectral wave parameters) of the SWAN model (Jan. 1992 to Dec. 2011). SWAN model (bulk and spectral wave parameter) outputs for extreme wave conditions. Output from the Delft3D-FLOW model for currents and water levels (1992 to 2011). Data from the HARMONIE model on which Deltares calculated extreme wind speeds. Is it further possible to obtain measured data from the SWB and SWC points? | 2015-04-08 | In response to questions 1/3/4: Time series for the reference points of each wind farm site will be made available via the website of RVO. In response to question 2: In Appendix B.3 of the metocean report, information on variance of extreme wave parameters over the sites is provided. Possibly these graphs provide the information required. In case parties require specific additional metocean parameters which are not provided in the metocean studies, the originator of the metocean studies (Deltares) can be contacted in order to discuss possibilities to make this data available. In case such a request to Deltares would generate data that is of common interest for developers preparing a bid for any of the Borssele wind farm sites, RVO and Deltares have agreed that these requests could be carried out under the assignment between RVO and Deltares, one and another dependent on the additional costs for making this data available and the added value of this data.
20 | Studies | GIS data | Geodata | We are searching for the geodata (GIS) published at the map in Figure 3.3 (sand extraction zones) of the Borssele EIA Scoping report (Notitie reikwijdte en detailniveau Milieueffectrapport kavelbesluiten Borssele). Could you please make the data available on the rvo.nl<http://rvo.nl/> homepage? | 2015-04-08 | All GIS data available within RVO regarding the Borssele Wind Farm Zone is / will be made availble through the Website of RVO: http://offshorewind.rvo.nl/studiesborssele In case parties require additional GIS information in the area surrounding the Borssele WFZ, a specific request for this data can be made through: http://www.noordzeeloket.nl/en/spatial-management/geographic-information/index.aspx
21 | Studies | Metocean study | Availability data | 1. The (metocean) reports reference and excel file containing eg. joint occurrence tables – these excel files have not been provided on the website. 2. Time series data have not been made available on the website – these will be required for assessment of adverse weather In various construction scenarios. | 2015-04-08 | The excel data files are available via the RVO website: http://offshorewind.rvo.nl/studiesborssele Time series for relevant parameters will be published at the same location on short notice.
22 | Studies | Metocean Campaign | Winner and timeline | Is the party selected for the Metocean campaign officially known? What timeline is foreseen regarding the start-up of the campaign? | 2015-04-08 | For the Metocean campaign, an award decision has been taken. Once the contract is signed the contractor will be made public. The start-up is planned in April 2015.
23 | Studies | Data sources |  | The Belgium database http://www.meetnetvlaamsebanken.be/ contains metocean data. Historical information is available at: http://www.kustdata.be/Default.aspx?Page=Security\Login&L=nl. The Belgium government charges a fee for downloading this data. Can RVO.nl provide free access to this information? | 2015-03-06 | ​RVO.nl has provided a metocean desk study (Deltares)​, is in the process of procuring a wind resource assessment​ ​and ​h​as planned a metocean measurement campaign. You are free to use other sources, but RVO.nl will not assist herein.
24 | General | Coordinates | PSD & NRD | On page 16 of the Project and Site Description the coordinates of the outer corner points of the Borssele wind farm zone are described. These are not equal to the detailled coordinates that are mentioned in Memorandum Scope and Level of Detail (NRD). There are less coordinates and the piloting area in the east of Site I is cut out. Also safety zones for cables and pipelines seem to be different (see wind farm site IV). Could you inform me on the correct coordinates of the: -Borssele wind farm zone -All four wind farm sites -Safety zones of pipelines cables and other exclusion zones | 2015-02-12 | In the Project and Site Description (PSD) reference is made to the memo 'Site Investigations Zones, December 2nd 2014' with all relevant coordinates of the Borssele site. This memo presents the most up to date information concerning the coordinates, site division, parcel division, infrastructure, safety zones, piloting zone and wind farm site boundaries. This memo wasn't attached with the PSD, but can be found at: http://offshorewind.rvo.nl/file/view/30829692/memo-coordinates-boundaries-sites-investigation-zones-rvonl The number of coordinates presented in the PSD is less than in the EIR (NRD), see the memo for details. Futhermore, it must be noted that by mistake, the site numbering in the annex of the EIR is reversed. Regarding the location I also refer to the memo. It's true that the SeaMeWe cable ( the cable from NNE directing SW that crosses Site I and III) is not displayed correctly in figure 3 of the PSD. The correct location is shown in the memo.
25 | Studies | Site investigations | Equipment Geophysical Survey | Could information be provided regarding the type of sub-bottom profiling equipment to be used during the geophysical survey. The variable water depth (10 to 40 metres) and possibly complex geology suggests that the use of a single system may not be optimal throughout. If this has not already been done it is recommended that detailed consideration is given to the selection of sub-bottom survey systems in order to optimise data acquisition and avoid the necessity to re-shoot the survey at a later date. It could prove advantageous to mobilise a range of systems and run test lines in order to be able to select an appropriate solution. A 2D High Resolution Seismic (2DHRS) digital survey system is likely to provide the best quality data for interpretation, Ground Model development, scoping the geotechnical works, foundation selection and FEED purposes. | 2015-02-10 | The choice of tools was left to the selected geophysical contractor (for Site 1 and 2 this is Deep).The scope of work required the sediments to be imaged to at least 80m below seabed but map the fine detail in the near surface sediments. This is what defines the instruments to be used and not the water depth of 10-40m (though this does have an influence). Detailed consideration was done by DEEP and the Project Plans and with that equipment selection were reviewed by two independent experts in the field. (RPS energy and Reynolds International). Deep has decided to use the following equipment: 1. Innomar SES-2000 parmetric sub-bottom profiler 2. Geo Marine Systems Ultra-High Res multi-channel streamer (with the following components: 48 channel Ultra hi-res streamer system, Geo-Source 200 LW sparker and 2000 X Geo-Spark HV power supply) We have understood both have been demonstrated to be a suitable tool for wind farm surveys as it has been demonstrated to achieve the required depth and resolution of data on a number of renewable projects in the North Sea and elsewhere. All geophysical survey works including the multi channel sparker and the sub bottom profiler survey have been completed. Preliminary results show that the both instruments combined provide required results up to 80m depth including the mid range from 10-40m BSB, critical for foundation design.
26 | Studies | Site investigations | Ground model | The Ground Model management and robustness from an project early stage is important and this will be further improved upon integration of the intrusive (ground trothing) geotechnical data. Development of the Ground Model throughout this process will facilitate detailed design.Comments concerning most favourable development areas and foundation options have been requested, although at this stage with such limited information this has not been possible, although the seabed topography is clearly more challenging for both WTG siting and cabling in some areas than others.” | 2015-02-10 | The Ground model will indeed be developed as the geophysics and geotechnics seek to inform and refine the Geological model, the model is intended to be a robust one with the information gathered and will be subject to peer and expert review as well as review by DNV-GL to confirm compliance where applicable. At this stage with no clear idea on turbine location and field layout, Geophysical lines plans and Geotechnical sampling is general, designed to make best use of the time and resources available. The Ground Model will be suitable for area selection based on suitability of ground conditions and e.g. FEED however it will be up to the Developer to assess if the data is suitable for more detailed foundation design based on selected field layout.
27 | General | Project and Site Description | Bathymetry | In the recent document "Borssele Wind Farm Zone - Project & Site Description" (on the website http://english.rvo.nl/topics/sustainability/offshore-wind-energy/borssele-wind-farm-zone) a detailed bathymetry-image of the Borssele area is shown in § 4.4 on p. 18. The caption states that the data is dated from 2010. In expectation of recent geophysical measurements in the project area, hereby already a formal request to digitally provide the bathymetry-data. Can you digitally provide concerning bathymetry data of 2010 or more recent measurements so we can place further project considerations on a more suficient background? | 2015-02-10 | Bathymetry data as used in the morphodynamical report produced by Deltares can be found at the following location: http://offshorewind.rvo.nl/file/view/31167462/morphodynamical-desk-study-msbl-rsbl-bathymetry-1999-2001-and-2010 Currently the geophysical site investigation of wind farm sites 1 and 2 has been completed. The bathymetry data obtained through this survey will be published on the RVO portal as soon as the review process of the results has been completed.
28 | Workshops | Wind measurement program assessment | Publication | When will the ‘Wind Measurement Program Assessment’ be published? | 2015-02-06 | The wind measurement program assessment can be found at the following location: http://offshorewind.rvo.nl/file/view/31040402/assessment-wind-measurement-program-north-sea-dnv-gl
29 | Workshops | Wind measurement program assessment | Offers - consultation meeting | Will the Netherlands Enterprise Agency (RVO.nl) organize another consultation meeting (after 27 February) to present all offers for carrying out wind measurements? Will the offers be made public? Can interested parties be involved in the evaluation? | 2015-02-06 | The review of the offers will take place internally. Because the procedures of a public EU tender are really strict, the process of reviewing is dictated by EU tender rules and laid down in the tender documents for the wind measurements. See below the link to the tender documents as published on Tenderned. In these documents you can find information on the review process of proposals. https://www.tenderned.nl/tenderned-web/aankondiging/detail/documenten/akid/a5d4d35058af70971a3977d6c4e21e33/pageId/D909B/huidigemenu/aankondigingen/da/false/cid/92389/cvp/join
30 | Studies | Geological desk study | Maps | Is it possible to receive the maps that would be available under Appendix I? | 2015-01-28 | The document including annexes is available at the following location: http://offshorewind.rvo.nl/studiesborssele