## Q&A's sector
Q&A log on offshorewind.rvo.nl - Tender wind farm zone Hollandse Kust (zuid)
Last update: 20170616
Number | Page | Subject | Sub subject | Question | Date response | Response
31 | General | Decommissioning | Decommissioning Start | In section 5.3.3 on page 51 in the Project & Site Description it is stated that: “Decommissioning can start latest end of year 25 and should be completed within two years maximum after the power generation operations have stopped, but at the latest in the 30th year.” Can you clarify if the sentence is correct or should it state “Decommissioning can start no earlier than end of year 25…”? | 2017-06-16 | The description in the Project and Site Description (PSD) is not correct. The sentence: “Decommissioning can start latest end of year 25 and should be completed within two years maximum after the power generation operations have stopped, but at the latest in the 30th year.” Must be replaced by: “Decommissioning can start end of year 25 earliest and should be completed within two years maximum after the power generation operations have stopped, but always within the term of the validity of the permit, in this case in the 30th year.” We will correct the PSD accordingly.
30 | General | Construction of the wind farm | Regulations during construction | These questions concern the regulations during the construction of the offshore wind farm: 1) Is a guard vessel to secure the construction site and passing traffic mandatory? 2) With reference to the Water Decree, art. 6.16h: Who is responsible for identification marks and beacons of the construction site? 3) Who pays for guard vessel(s), identification marks and beacons? | 2017-05-15 | 1) During construction activities guard vessel(s) are mandatory, at least one, in many cases two. This is subject to approval by the Netherlands Coastguard. 2) The site developer is responsible for the identification marks and beacons of the construction site. 3) The costs for guard vessel(s), identification marks, beacons and the mandatory Notice to Mariners are at the expense of the site developer.
29 | General | Metocean Study | Turbulence intensity | This is a question to the Metocean study on Hollandse Kust Wind Farm Zone: Chapter 10.1.4 Conversion between time scales: You are recommending the ISO 19901 wind spectra (Frøya spectra). You are recommending the same turbulence intensity at both 10 and 100 m above mean sea level? Then you will end up with too strong gust at the heights above 10 m? There is no doubt that wind turbulence shall decrease with height? That means that Figure 10.4 and Table 10.7 only is valid 10 meter above mean sea level? This table is used to calculate wind gust at all heights. In my opinion a 1-hour mean wind speed at 100 m of 39.6 m/s corresponds to 10-minute mean of 42.0 m/s (you have 44.3 m/s) and a 3 s gust of 49.2 m/s (you have 58.3 m/s). Can you please clarify? | 2017-05-12 | Your observations are correct. Netherlands Enterprise Agency and DHI have issued a revised report that has been made public on May 11th, 2017. Please refer to PDF page 16 ‘Revision History’ for the comparison between V2.2 and V2.1. Data in the Metocean Database are correct and do not need an update.
28 | General | Floating LiDARs | Location; serial numbers;listed serial | We have been unable to find the following information on the RVO web pages regarding the Hollandse Kust floating Lidars. Please could you provide the following information: 1) Confirmation of the location of both HKZA and HKZB in Lat/Long; 2) Confirmation of both of the device’s serial numbers; 3) The serial listed in the header of the HKZA file notes it as being “WS149”, however this corresponds to the FLiDAR1 at Borssele. As the time series for these two devices overlap it seems unlikely that they are the same device. | 2017-05-04 | Please find confirmation of the locations: a) In the Fugro Monthly Data reports. Locations can be found in paragraph 1. Introduction. b) In the Deltares Monthly Validation reports. Locations can be found in paragraph 1. Introduction. 2) The serial numbers of the devices which have been used can be found in the reports and data. Please note that -due to buoy swaps- positions can change in time within Wind Farm Zones (Hollandse Kust (zuid) and Hollandse Kust (noord)) and between Wind Farm Zones (Borssele, Hollandse Kust (zuid) and Hollandse Kust (noord). 3) WS149 is used in Borssele Wind Farm Zone, Hollandse Kust (zuid) and in Hollandse Kust (noord). WS149 is only used at one location at the time.
27 | General | Wind Resource Assessment | Correcting coordinates | Regarding table 13, page 36 of the HKZ Wind Resource Assessment (HKZ_20161222_Ecofys_Hollandse Kust (zuid) Wind Resource Assessment-F.pdf), can you please check the coordinates HKZ2 and HKZ4? | 2017-04-06 | The coordinates for points HKZ2 and HKZ4 prove to be inversed in Table 13. That error is also reproduced in the header for the Excel spreadsheets for points HKZ2 and HKZ4. The error does not affect any of the data or calculations. All results presented in the report and spreadsheets are correctly identified by site name. The metadata will be updated in a revised excel file and report.
26 | General | Inactive cables | Possible restrictions | Please clarify if there are any restrictions in relation to the inactive cables located in HKZWFS? | 2017-04-06 | There are no restrictions in relation to inactive / abandoned cables.
25 | General | Construction vessels | Positioning of construction vessels | Please clarify if positioning of construction vessels (including jack-ups and anchors) during site construction outside the HKZWFS boundary lines is allowed? | 2017-04-06 | This is allowed if positioning (jack-up and anchoring) is done in open sea. Positioning in maintenance zones or safety zones of existing cables and/or pipes and/or installations is prohibited unless agreed upon otherwise in a proximity agreement with the owner.
24 | General | Maintenance Zone | Positioning of anchors | Please clarify if positioning of anchors in the maintenance zones during site construction is allowed. If not, is positioning of anchors on the opposite side of the maintenance zone allowed with free positioning of the anchor cables in the maintenance zone? | 2017-04-06 | Anchoring in the maintenance zone of an existing cable or pipe is prohibited, unless agreed upon otherwise in a proximity agreement with the owner of the cable or pipe. Whether anchoring on the opposite side of the maintenance zone is allowed depends on the area. If this is open sea then anchoring is allowed, for the anchoring cables there is no restriction
23 | General | Final Wind Farm Site decisions | Appeals | Have appeals been made against the final Wind Farm Site Decisions WFS I and II Hollandse Kust (zuid)? If so, can you disclose who did so and on which basis? | 2017-03-09 | Seven parties have made an appeal at the Council of State. More information is to be found here: http://www.rvo.nl/subsidies-regelingen/bureau-energieprojecten/lopende-projecten/windparken/woz-kavels-holl-kust-zuid-i/i (Dutch only)
22 | General | Scour conditions | Scour conditions | Can you describe scour conditions to be expected at Hollandse Kust (zuid) for typical structure types (like monopiles)? | 2017-02-23 | The Netherlands Enterprise Agency will prepare for a concise report on scour conditions to be expected at Hollandse Kust (zuid), to be published Q2 2017.
21 | General | Planned COAM cable | Details on the COAM cable | Could you please provide more details on the planned COAM cable, hereunder planned installation schedule and any associated potential implications and/or interfaces during the construction and operation of the HKZI & II wind farms? | 2017-02-07 | The planning of the installation of the consented COAM telecom Cable, owned by PiPiper, is currently unknown.
20 | General | Metocean Data | Metocean timeseries | I have a question related to the Metocean data available for the Hollandse Kust (Zuid) site. For this site only Metocean reporting is available while for the Borssele sites also data in timeseries (from hindcasting) is available. These are the timeseries used to calculate the normal sea states and contain amongst others: wave height Hs, wave period Tp, wave direction, wind direction, wind speed. Would it be possible or is it planned to make these timeseries also available for Hollandse Kust (Zuid)? The availability of these timeseries would allow for a more detailed design assessment, reduce design conservatisms and therefore benefit the design of the support structures. | 2017-01-26 | These time series will be available through the metocean database. This metocean database will be published beginning of February 2017 and can be accessed from offshorewind.rvo.nl
19 | General | Site coordinates | Differences in coordinates | Two coordinates in the official Wind Farm Site Decision differ from those in Annex C: Boundaries and Coordinates (Part of Project and Site Description). | 2017-01-20 | The coordinates in Annex C: Boundaries and Coordinates (Part of Project and Site Description) and the Base Map (GIS.MPK file) are correct. There is an error in the publication of the Wind Farm Site Decision published in the Gazette on 16th December 2016. A rectification has been published in the Gazette of 20th January 2017 (in Dutch): Subject: Coordinates of the infield cable entry zone HKZWFS I: Point No. CE_02 Easting must be 571,497.2 and not 571.492,2. Point No. CE_05 Northing must be 5,797,511.9 and not 5.795.511,9
18 | General | Site coordinates | Differences in coordinates | We have noticed a discrepancy between the published draft Wind Farm Site Decisions I & II Hollandse Kust (zuid) and the PSD Appendix C: 'Boundaries and Coordinates version November 2016'. Which set of coordinates should be considered leading? | 2016-12-09 | The PSD Appendix C: 'Boundaries and Coordinates version November 2016' shows some small deviations from the draft Wind Farm Site Decisions. The coordinates in the final Wind Farm Site Decisions will be based on this memo. Nevertheless only the official final Wind Farm Site Decisions are legally binding and are expected to be published in December 2016.
17 | General | Windturbines and weather circumstances | Certification | The Water Decree states in article 6.16g: Section 6.16 that a wind turbine and any other part of the wind farm must be sufficiently strong. A statement about this must be compiled by an independent expert who has carried out tests in accordance with a proven system of standards relating to the design and installation of a wind farm.Can you enhance on the interpretation and the link to the project certification? Which Certification Bodies will be accepted as independend experts? | 2016-12-02 | Paragraph 1, section 6.16g can be covered by the certification phases design, which relies on the design basis (‘design basis’ and ‘design’ in diagram below). Paragraph 2, section 6.16g demands to prove that the construction/installation is safe before going into operation. For this purpose certification phases ‘manufacturing’, ‘transport & installation’ and ‘commissioning’ are designed. See diagram above. E.g. within DNVGL-SE-0190, for each certification phase a Statement of Compliance can be provided. In this way also the progress can be documented. The wind power plant assets to be covered within 6.16g are the wind turbines and the infield cables. The substation, export cables and control station are not covered within 6.16g. The certification body must be independent. It is industry standard to use a certification body accredited by a European national accreditation body. Certification by a non-accredited body will not be accepted.
16 | General | Safety zones | Jack-up operations | Please clarify if jack-up operations within the 500 m safety zone are allowed during installation of the wind farm as well as during the operational phase for potential repair and maintenance works? | 2016-11-11 | Jack-up operations are allowed in your own safety zone but prohibited in a maintenance zone of an existing cable or pipe. When a safety zone overlaps a maintenance zone, jack-up operations are prohibited unless agreed otherwise in a proximity agreement.
15 | General | Water Decree; transformer station | Certification of transformer station | The Water Decree includes two articles about the certification of a substation. Please explain if the future operator of a wind farm should submit design certificates covering the transformer station. | 2016-11-11 | Developers and operators of future wind farms are not responsible for the (TenneT) platforms (transformer stations). The text referred to applies to existing wind farms only.
14 | General | UXO removal by contractor | UXO removal by contractor | Who is allowed to remove UXOs and who is bearing the costs? | 2016-11-11 | Royal Netherlands Navy is solely responsible for the disposal (removal) or relocation of any UXO encountered. Other contractors are not allowed to do so. The authorities cover the cost of UXO removal.
13 | General | Requirements | Operational modifications | In Germany, new wind farms are required to modify operations of those turbines whose wake effect would exceed the assumptions used in designing previous installed wind farm(s). Does the Netherlands have now, or does it plan to have, a similar requirement as in Germany? | 2016-11-11 | There are currently no similar requirements foreseen.
12 | General | Crossing and proximity agreements | Private agreements required? | Are crossing and proximity agreements or any other agreements private law required with regards to the offshore wind farm? | 2016-11-11 | Crossing, proximity and any other agreements under private law are not mandatory.
11 | General | Soil samples | Future use soil samples | Will the soil samples from the geotechnical boreholes at the HKZ site be stored for future use? If so, for how long? | 2016-11-11 | The remaining samples will be stored until the winners of the tenders are known, and handed over to them.
10 | General | Wind Farm layout | Yield optimisation | Can you please confirm that the developer – with respect to project area borders, safety zones, etc. – has full freedom to make a wind farm layout based on yield optimisation; for example a curved layout or with a dense border of turbines versus a layout where turbines are in straight lines? | 2016-11-11 | Confirmed. There will be no other restrictions to the wind farm lay out other than the general rules and the design envelope. Restrictions to the lay out itself are not foreseen.
9 | General | Wind Farm Site Boundaries | Distance to boundaries | The Wind Farm Site Boundaries are not always exactly 500 metres from a cable, does this have any impact? | 2016-04-15 | The boundaries of the Wind Farm Sites as published in the Wind Farm Site Decisions are binding. For telecom cables a maintenance zone of 1,000 metres applies. In some cases the telecom cables and pipelines are not exactly in the middle of this maintenance zone due to small bends.
8 | General | Certification | Project certification body | Will there be a project certification body or comparable entity involved over the lifetime of the project, by some sort of periodic inspections? | 2016-02-23 | This is not foreseen.
7 | General | Standards and guidelines | Standards and guidelines | Which standards, recommendations, guidelines, obligations are to be followed for design, manufacturing, installation, commissioning and operation of the WTG, Foundation, Cable, interfaces? | 2016-02-23 | Internationally recognised standards. It is not possible to present a complete overview.
6 | General | Water Decree | Ministerial Order | Article 6.16g (4) of the Water Decree says "A ministerial order may lay down rules on the content of a declaration referred to in the second paragraph." Does such ministerial order, or a draft or a term-sheet, already exist? | 2016-02-23 | No, it does not. A brief guideline will be drafted that outlines which data in the various plans has to be submitted.
5 | Studies | Archaeology | Exclusion zone | Are you able to inform about the size of the exclusion zone around a potential object of archaeological value? | 2016-02-22 | In general a buffer or safety zone of 100 metres around an archaeological object or an object with an archaeological expectation is to be defined, in which no activities such as trenching or anchoring are allowed. If additional research shows that the object has no archaeological value, the location and the buffer zone can be omitted.
4 | General | Water Decree | Cables burial depth | Are there any requirements for inter array cables burial depth? The Water Decree only specifies this for Export cables to be 1.0 meter. Would the developer for instance be allowed, if preferable from a risk perspective, not to bury the cables? | 2015-12-10 | There are no requirements for the burial depth of inter array cables.
3 | General | European Species Licence | European Species Licence | Will a European Species Licence be required for any impact piling work or does the Kavelbesluiten cover any such requirement determined by the Habitats Directive? | 2015-12-10 | The Wind Farm Site Decision covers all requirements. No other permits / consents are needed.
2 | General | Water Decree | Export cables | Within the Water Decree there are a number of conditions stated for “export cables”. Please can it be confirmed that the term export cable only refers to TenneT cabling and the term does not include inter-array cabling within a wind farm? | 2015-12-10 | Confirmed.
1 | General | Wind farm layout | Procedure lay out approval | In case of any layout requirements the Tenderer needs to have his layout approved by the competent authority before tender submission in order to submit a firm bid as layout restrictions will impact the business case. What will be the procedure for layout approval during the tender process? | 2015-05-22 | The bandwidth and other restrictions defined in the wind farm site decision must be respected. There is no pre-approval procedure foreseen.