## Q&A's sector
Q&A log on offshorewind.rvo.nl - Tender wind farm zone Hollandse Kust (noord)
Last update: February 10th, 2020
Number | Page | Subject | Sub subject | Question | Date response | Response
28 | General | Military shooting range | Status military shooting range | The Hollandse Kust (noord) Wind Farm Site Decision V states that the military firing range at Petten will be reoriented so it no longer overlaps with the site. The shooting direction will change from west to north-west, outside of Site V. What is the current state of affairs regarding this procedure? | 2020-02-10 | The procedures for reorienting the firing range have not yet been completed. However, they are expected to be completed before the construction of the wind farm will commence. Irrespective of the reorientation of the firing range on shore, the shooting direction will be permanently changed before the construction of the wind farm will commence (as of 1 July 2022 or the date on which the wind farm developer’s permit comes into effect) to ensure that the unsafe zone at sea no longer overlaps with Site V. The reorientation of the firing range will not interfere with the timely start of the construction and use of the wind farm. The Ministry of Economic Affairs and Climate Policy, as well as the Ministry of Defence, will also draw up a communication protocol for the period in which location studies will be conducted prior to the construction of the wind farm. The goal of this communication protocol for activities in military areas is to avoid conflicts between activities carried out by or on behalf of the wind farm developer and activities carried out by the Dutch army in Dutch military zones. As a result, the location studies can be carried out safely. Finally, the Ministry of Defence has a permit for a maximum of twenty shooting days a year.
27 | General | Unidentified obstructions | Unidentified obstructions in the PSD | Figure 4b in the Project and Site Description (PSD) contains a large number of obstructions in the northeastern part of the HKNWFZ. Can you please provide information about the nature of these obstructions and potential associated exclusion zones? | 2020-01-06 | Figure 4b in the PSD is referring to the Archaeological Desk Study (phase I) which is unfortunately causing some confusion. The contacts in this Figure 4b were reported by Rijkswaterstaat in 2013 for the sand extraction area in the northeast corner of the HKNWFZ. The results of the Archaeological Desk Study are superseded by the Archaeological Assessment (phase II) of the geophysical results. In this geophysical survey some of the reported obstructions were detected and reported as debris or boulders while most of them were not detected. All results are described in the Archaeological Assessment (phase II): https://offshorewind.rvo.nl/file/view/55040115/Report+-+Archaeological+Assessment+%28Phase+II%29+-+Periplus+Archeomare.
26 | General | Infield cables | Infield cables connecting two WTGs | Please confirm that infield cables connecting two WTGs are allowed to be installed within the cable entry zone, even if this is outside the WFS boundaries. | 2019-12-20 | Infield cables connecting two WTGs are not allowed to be installed outside the WFS boundaries. Of course it is allowed to use the cable entry zone within the WFS boundaries to connect two WTGs.
25 | General | Buffer zone | Restrictions in the buffer zone | Are construction vessels and jack up operations allowed in the buffer zone around the Wind Farm Zone? | 2019-12-20 | The safety zone is intended to regulate the access of ships to the wind farm. Work vessels can always cross this zone and jack up vessels are permitted to carry out work within the zone.
24 | General | Abandoned boreholes | Restrictions regarding abandoned boreholes | Is it allowed to install inter array cables inside the 100 meter buffer zone around the two abandoned boreholes, as long as the array cables will not be placed on the borehole? | 2019-12-09 | No, it is not allowed to install inter array cables inside the 100 meter bufferzone around the two abandoned boreholes.
23 | General | Lay out wind farm site HKN | Military shooting range | Can you confirm that the current military shooting range partly overlapping with the northern part of the HKNWFZ will have no impact on either wind farm site investigations, construction works or operation? | 2019-10-25 | The firing range of the military training ground is currently under discussion between the Ministry of Defence and Waterboard (Hoogheemraadschap). The outcome is expected before start of construction of the wind farm. At this point it has no impact on the site investigations.
22b | General | Geotechnical Survey | Missing data? | Update of question 22a | 2019-09-20 | RVO.nl has added the raw SCPT data (without stacked time traces) to the geotechnical deliverables. You can find them here: https://offshorewind.rvo.nl/questions/view/55040224/hkn-geotech-misses-data-scpt-tests-updated-september-20-2019
22a | General | Geotechnical Survey | Missing data? | The Hollandse Kust (noord) Geotech data does not contain measurement records (timeseries) of the SCPT tests that were performed. Is it possible to provide the raw and stacked time traces (for instance in .ASCI or .txt files), and any information regarding signal sampling rate, time initialization, explanation of file names, etc? | 2019-08-29 | It is confirmed that this raw SCPT data is not in the current delivery. RVO.nl will contact the geotechnical contractor, aiming for a delivery of raw data (without stacked time traces) end of September 2019 latest
21 | General | Dredging |  | What is the status of dredging zone Q5J in the northeastern part of the Wind farm Site? What are the consequences for the development and future operation of the windfarm? | 2019-08-20 | Reference is made to status of Q5J in the Geophysical site investigation survey 2017 (https://offshorewind.rvo.nl/file/download/55039463), among others in 2.4.6 Dredged Zones. The dredging zone It is licensed until 1st of July 2019 and can be dredged to a maximum depth of 2 m. After the expiration date no extra requirements / limitation to this area apply.
20 | General |  |  | Reference is made to the EIA information stated on The Netherland Enterprise Agency website, "no separate document will be published because the information is already available online". Is the EIA summary available in the English language ? and if ‘yes’, where? | 2019-08-20 | There is an English summary of the EIA available. It is a part of the EIA that is published on the website of Bureau Energieprojecten https://www.rvo.nl/onderwerpen/bureau-energieprojecten/lopende-projecten/windparken/wind-op-zee-kavels-hollandse-kust-noord-v/fase-1
19 | General | Cables |  | Cables 5, 7, 13 and 6 in fig 4.1 in Appendix C) are not shown on the "Hollandse Kust" webmap which is available through offshorewind.rvo.nl. What is the source of the information and what does it say about the level of certainty on the location of these cables? Would it be possible to send a GIS file or a link to this data ? | 2019-08-20 | The information in Appendix C is based on the geophysical survey in 2017, the report, appendices and order form for the geophysical data is to be found here: https://offshorewind.rvo.nl/soilnh (the as found data of the cables and pipelines is to be found in Appendix C).
18 | General | Cables | Telecom cable UK-Netherlands 14 (no. 5) | Telecom cable UK-Netherlands 14 (number 5, fig 4.1 in Appendix C) is stated as being active however the cable seems to terminate mid-way in the HKNWFZ. Please clarify. | 2019-08-20 | In the 5th August 2019 update of the PSD Appendix C the status of cable UK-Netherlands 14 (no. 5 in the Appendix) was changed from 'abandoned by end 2018' into the status active. During the geophysical survey this cable was detected partly (as presented in the PSD Annex C). Rijkswaterstaat can deliver on request the as laid data for the not detected part of this cable. Requests can be send to Servicedesk Data (CIV) e-mail: servicedesk-data@rws.nl
17 | General | Cables | Abandoned cables | What are the intentions wrt the inactive/abandoned cables within the HKNWFZ site (Ref Appendix C : cables 5 and 12) ? (e.g. Is it considered that the Concessionaire can cut/remove these cables as desired?) | 2019-08-20 | If needed, inactive/ abandoned cables can be cut or removed by the wind farm developer.
16 | General | Export Cable | Export cable | The export cable (TenneT) that crosses the HKNWFZ location (East to west) doesn’t seem to have a documented 500m boundary/corridor. Is it acceptable to have foundations and construction vessels closer than 500m to this cable (as long as the existing maintenance zone (stated in Appendix C) is not violated )? | 2019-08-20 | That is correct. TenneT decided to reduce the spacing between the cables to 200 metres. The spacing between the TenneT cable and the telecom cable remains 500 metres, hence the total zone between the two parcels is 500+200+500+500= 1,700 metres.
15 | General | Crossing Angles | Infield cable crossings | Are there any limitations on crossing angles in regards to infield cable crossings with existing ‘in-use’ cables / pipelines ? | 2019-08-20 | This is considered to be settled between the wind farm developer and the owner of the cable / pipeline. Please note in the Netherlands Exclusive Economic zone crossing and proximity agreements are not mandatory. Construction vessels are allowed within maintenance zones of cables and pipelines, jack up operations are prohibited. Foundations must be placed at least 0.5D from the Wind Farm Site boundaries, as overhanging of rotorblades in maintenance zones is prohibited.
14 | General | Construction vessels | Cable Entry Zones | Are construction vessels allowed in all locations of the cable entry zones ? | 2019-08-20 | Construction vessels are allowed within the whole Wind Farm Zone, with the restriction that jack up operations are prohibited in maintenance zones of existing cables and pipelines.
13 | General | Cable entry zones | Cable Entry Zones | What are the ‘cable entry zone’ requirements ? Can infield cables be placed outside the HKNWFZ boundaries if they are within the cable entry zones? | 2019-08-20 | The only restriction is that infield cables have to be installed within the WFS boundaries and the cable entry zones. No other restrictions (e.g. burial depth) apply.
12 | General | Telecom cable | Telecom cable UK-Netherlands 14 (no. 5) | Table 4.1 in Appendix C document (Appendix C_Memo_Boundaries_&_Coordinates_HKN_Hollandse Kust_noord_8 August_2019), contains telecom cable UK-Netherlands 14 (no. 5) with information that this is “Abandoned by end 2018”. Can you confirm this? | 2019-08-15 | Telecom cable UK-Netherlands 14 (no. 5) is still in use, contrary to the information in Table 4.1 in Appendix C document (Appendix C_Memo_Boundaries_&_Coordinates_HKN_Hollandse Kust_noord_08 August_2019). We have updated this Appendix, which now has version number F1.5 dated 15 August 2019.
11 | General | Wreck locations | Coordinates wreck locations | The coordinates of the wreck locations in the PSD, Appendix C (table 2.7) do not match with figure 2.5 (Page 11). Please confirm correct coordinates of these wrecks? | 2019-08-08 | There is an error in the coordinates of the wreck locations in table 2.7 of the PSD, Appendix C. The correct coordinates are: For wreck AV_01 Easting 590,712.0 and Northing 5,824,349.0; For wreck AV_03 Easting 588,397.0 and Northing 5,827,512.0. An updated version of PSD Appendix C has been published.
10 | General | Maintenance zone | Maintenance zone for export cables | The two export cables for the Hollandse Kust (west) Alpha platform are crossing the Hollandse Kust (noord) Wind Farm Zone. It seems that the maintenance zone for these cables is less than 500 metres. Is that correct? | 2019-08-08 | That is correct. TenneT decided to reduce the spacing between the cables to 200 metres. The spacing between the TenneT cable and the telecom cable remains 500 metres, hence the total zone between the two parcels is 500+200+500+500= 1,700 metres.
9 | General | Abandoned boreholes | Restrictions regarding abandoned boreholes | In the Wind Farm Zone two abandoned boreholes are identified (NITG numbers BQ040153 and BQ040144, see also PSD, Appendix C, table 4.20). Are there any restrictions for the lay out of the wind farm and installation of monopiles? | 2019-08-08 | Yes, the following restriction applies: 1) A bufferzone of 100 metres applies, the distance between the center of a (monopile) foundation and these boreholes must be at least 100 metres. Furthermore: 2) Overhanging of turbine blades in the bufferzone of an abandoned borehole (well) is allowed; 3) Rock dumping as scour protection for the (monopile) foundation(s) is allowed, assuming that the scour protection has a diameter of <25 metres; 4) Jack up operations in the bufferzone are allowed, with the condition that the legs will not be placed on the borehole.
8 | General | Metocean Desk Study | Bathymetry EMODnet data | For the model bathymetry EMODnet data has been used by DHI. The EMODnet data from 2016 has a resolution of 1/8 * 1/8 arc minutes, which is about 140m x 230m. The Metocean Database report indicates however in table 3.1 that the resolution of the EMODnet data is 0.125 minutes (1400m x 2300m). Figure 3.4 on the top left (see report) shows the used EMODnet data which appears to have a resolution of more than 500m. Has the EMODnet data been modified / made coarser by DHI, and if so why? | 2019-06-24 | Figure 3.4 (top) shows the scatter data from Fugro covering HKN combined with EMODnet after interpolation on the mesh (see text above Table 3.1).The mesh resolution at HKN is 400m and it gradually increases in size to ~600m at HKW, IJmuiden-Ver etc. At HKN, the Fugro bathymetry interpolated to a 50 m grid was used. So Fugro’s high resolution bathymetry was used where we have 400m resolution.The EMODnet data used for this study has a resolution of around 140m x 230m for HKN area (1/8 * 1/8 minutes); as the grid size is significant larger in this area (400m or larger), using the finer bathymetry data available via EMODnet (resolution of 1/16 x 1/16 minutes, grid size of around 70m x 115m) would not have a significant effect on the model results. NB: Please be aware that the 1400m x 2300m in Table 3.1 is not correct and should be 140m x 230m. Correct Table 3.1 is shown at this page: https://offshorewind.rvo.nl/questions/view/55040091/metocean-desk-study-bathymetry-emodnet-data-june-24-2019
7 | General | LiDAR data | Time Series of LiDAR data | Will you provide an agglomerated and processed time series of LiDAR data (wind speed & direction for the whole period) or should we download the datafiles in “raw” format from your website at 'HKN Metocean Campaign Data & Reports'? | 2019-05-20 | After 24 months of data collection we will provide a comprehensive 24-months report about the metocean campaign HKN. The agglomerated and processed time series of LiDAR data are included in this report. However, this report will be due delivered in August 2019. Until then it would be recommendable to download the ‘raw’ data files from the website.
6 | General | Geotechnical Survey | Planning of the results | When will the results of the geotechnical works for Hollandse Kust (noord) be available? | 2019-03-07 | The Hollandse Kust (noord) geotechnical results are planned to be disclosed in April 2019. Please note that an engineering ground model, which contains characteristic values of the Hollandse Kust (noord) Wind Farm Zone, is in preparation and scheduled for disclosure in Q3 2019.
5 | General | vertical reference system | LAT versus NAP | The vertical reference system used for Dutch sites and the site investigations is LAT. Can you explain why LAT was selected rather than NAP? | 2019-02-18 | LAT is used as a vertical reference for most of the site studies executed by RVO.nl (ETRS89 is used as the three-dimensional coordinate system) since this is the reference level most often used and commonly accepted. Exceptions are the studies and campaigns where explicitly stated different. In that case often MSL is used as a reference. Please find a conversion table to different (mean) astronomical tide levels at the HKZ and HKN site in chapter 9.2.2. of the metocean desk study. Normaal Amsterdams Peil (NAP) is not used by RVO.nl but NAP comes close to MSL.
4 | General | LiDARs | Validation LiDAR units | For the specific case of Hollandse Kust (zuid), there have been a number of floating LiDARs deployed successfully at the site. Validation reports are available online. These are the validation reports of the floating LiDARs (LiDAR mounted on buoy). Can you please also disclose the validation of the LiDAR units itself? | 2019-02-01 | As for Borssele Wind Farm Zone, for Hollandse Kust (zuid) and Hollandse Kust (noord) a number of floating LiDARs have been deployed successfully. The Performance Verification Reports for these LiDARs, which were used for Hollandse Kust (zuid) and (noord) Metocean Campaign, can be found via the link in column H. | Performance Verification Reports Zephir Lidars
3 | General | Connection | Connection between wind farms | Why is there no connection between IJmuiden Ver and Hollandse Kust (noord)? | 2019-01-21 | This is because the power transmission technology will be different. Hollandse Kust (noord) will be connected with AC power cables and IJmuiden Ver with DC power cables. Also, the route of IJmuiden Ver still needs to be investigated.
2 | General | Conditions for compliance | Marine coordination | Does the Netherlands have its own explicit conditions for compliance or is marine coordination, based on the European Directive 92/57/EEC and Directive 89/391/EEC, sufficient? | 2018-05-16 | Construction vessels themselves must comply with the (inter)national legislation, required for each specific type of vessel. The European Directives 92/57/EEC + 89/391/EEC are the responsibility of the ship owner/company. This is monitored by the Human Environment and Transport Inspectorate (ILT) and is subject to Port State or Flag State Control.
1 | General | Regulation during construction phase | Marine coordination | Is there any specific regulation applicable during construction phase, regarding marine coordination to protect construction vessels and personnel, as well as to manage other maritime traffic (e.g. freight transport and recreational craft), around the offshore construction zone? | 2018-05-16 | The Netherlands Coastguard (KWNL) specifies the conditions, which have to be included in the Operational Working Plan (article 6.16e Water Decree), to be delivered by the windfarmoperator. All seafaring vessels involved during either the survey, construction and/or operational phase of an offshore wind farm, must meet these requirements. Coordination of vessels, including construction vesssels, is the responsibility of the owner/captain. The Borssele Wind Farm Zone, for example, is already highlighted in naval charts as 'Wind Farm Precautionary Area'. Prior to actual construction of the wind farm, the area will be sealed off by signposts and buoys, a notification in the Notices to Mariners (NtMs), and distribution of navigational information via NAVTEX by KWNL. In addition, the use of a guard vessel is mandatory during the construction phase. Furthermore, future owners of the wind farm sites and the Offshore High Voltage Substation (OHVS) platforms, TenneT, must remain in close contact.