## Q&A's sector
Q&A log on offshorewind.rvo.nl - Tender wind farm zone Hollandse Kust (zuid)
Last update: 20190228
Number | Page | Subject | Sub subject | Question | Date response | Response
44 | General | Metocean Campaign | Directional Wave Spectra Data | How have the directional wave spectra data displayed in the video files (..Spectra_Comparison.mp4) located in the folders “\03 - Validation report” of each of the data folders under “Metocean Campaign Data & Reports” been calculated? | 2019-02-28 | The 2d wave spectra are calculated from the WaveSpectraComponents file. “The heave spectra” refers to hspec (spectral density) in the WaveSpectraComponents file, together with the fourier coefficients (a1,b1,a2,b2) constitutes the basis for calculating directional wave spectra using the Maximum Entropy Method as was done to produce the plots and video files for the monthly and campaign reports. | https://offshorewind.rvo.nl/file/view/55039937/Maximum+Entropy+Estimation+of+the+Directional+Distribution+in+Ocean+Wave+Spectra%2C+Chapter+3
43 | General | LiDAR | 10-minute LiDAR signal “number of packets” | Could the contractor of the Hollandse Kust (zuid) Metocean Campaign include the 10-minute LiDAR signal “number of packets” to the following processed data packages: https://offshorewind.rvo.nl/file/view/55039497/Processed+Data+HKZA https://offshorewind.rvo.nl/file/view/55039498/Processed+Data+HKZB At the moment this availability signal is not present in the two text files “HKZ_20180927_Fugro_Metocean Buoys HKZB WindResourceSpeedDirectionTIStat_F.csv” and “HKZ_20180927_Fugro_Metocean Buoys HKZA WindResourceSpeedDirectionTIStat_F.csv”. | 2019-02-26 | It is not possible in the course of the Hollandse Kust (zuid) III and IV tender preparation to provide these ‘number of packets’ since the number of samples in average statistic was not made part of the processed data. However, and for your information, the values all had a minimum of 18 samples (packets) in each 10 minute average (wind speed or direction), otherwise the 10 min average would be NaN.
42 | General | vertical reference system | LAT versus NAP | The vertical reference system used for Dutch sites and the site investigations is LAT. Can you explain why LAT was selected rather than NAP? | 2019-02-18 | LAT is used as a vertical reference for most of the site studies executed by RVO.nl (ETRS89 is used as the three-dimensional coordinate system) since this is the reference level most often used and commonly accepted. Exceptions are the studies and campaigns where explicitly stated different. In that case often MSL is used as a reference. Please find a conversion table to different (mean) astronomical tide levels at the HKZ and HKN site in chapter 9.2.2. of the metocean desk study. Normaal Amsterdams Peil (NAP) is not used by RVO.nl but NAP comes close to MSL.
41 | General | Vertical reference | Vertical reference WRA | Can you please confirm that the vertical reference of the datasets of the HKZ WRA as disclosed at https://offshorewind.rvo.nl/file/view/53817132/Calculated+Wind+Climate+WRA+2+HKZ+WFZ+-+Ecofys and https://offshorewind.rvo.nl/file/view/51102772/Calculated+Wind+Climate+WRA+1+HKZ+WFZ+-+Ecofys is Mean Sea Level? | 2019-02-18 | It is confirmed that the vertical reference of these datasets is Mean Sea Level (MSL).
40 | General | Lidar validation | Metocean campaign | For the specific case of Hollandse Kust Zuid, there has been a number of floating LiDARs deployed successfully at the site. Validation reports are available online. These are the validation reports of the floating LiDARs (LiDAR mounted on buoy). Can you please also disclose the validation of the LiDAR units itself? | 2018-12-18 | The Performance Verification Reports of the Zephir LiDARs can be found in the link in field H. These are the Performance Verification Reports used for a) the LiDARs used at the Borssele WFZ metocean campaign, b) the LiDARs used at the Hollandse Kust (zuid) metocean campaign and c) the reference LiDAR at Froya. | https://offshorewind.rvo.nl/questions/view/55039876/lidar-validation-december-18-2018#answer-55039877
39 | General | Conditions for compliance | Marine coordination | Does the Netherlands have its own explicit conditions for compliance or is marine coordination, based on the European Directive 92/57/EEC and Directive 89/391/EEC, sufficient? | 2018-05-16 | Construction vessels themselves must comply with the (inter)national legislation, required for each specific type of vessel. The European Directives 92/57/EEC + 89/391/EEC are the responsibility of the ship owner/company. This is monitored by the Human Environment and Transport Inspectorate (ILT) and is subject to Port State or Flag State Control.
38 | General | Regulation during construction phase | Marine coordination | Is there any specific regulation applicable during construction phase, regarding marine coordination to protect construction vessels and personnel, as well as to manage other maritime traffic (e.g. freight transport and recreational craft), around the offshore construction zone? | 2018-05-16 | The Netherlands Coastguard (KWNL) specifies the conditions, which have to be included in the Operational Working Plan (article 6.16e Water Decree), to be delivered by the windfarmoperator. All seafaring vessels involved during either the survey, construction and/or operational phase of an offshore wind farm, must meet these requirements. Coordination of vessels, including construction vesssels, is the responsibility of the owner/captain. The Borssele Wind Farm Zone, for example, is already highlighted in naval charts as 'Wind Farm Precautionary Area'. Prior to actual construction of the wind farm, the area will be sealed off by signposts and buoys, a notification in the Notices to Mariners (NtMs), and distribution of navigational information via NAVTEX by KWNL. In addition, the use of a guard vessel is mandatory during the construction phase. Furthermore, future owners of the wind farm sites and the Offshore High Voltage Substation (OHVS) platforms, TenneT, must remain in close contact.
37 | General | Laboratory testing programme | Remaining samples | Can you disclose an overview of the remaining samples of the laboratory testing programme, that will be handed over to the winner(s) of the application for the permits? | 2017-12-11 | This overview can be downloaded via the link in field H. | Overview remaining samples HKZ I&II
36 | General | Combined Wind Resource Assessment | Measurements of HKZA and HKZB | There seems to be a consistent difference of ~5° in the wind direction measurements of HKZA and HKZB. Is there any explanation, given the small distance between the 2 positions? | 2017-11-27 | Ecofys WTTS confirms that the two wind direction measurements (HKZA and HKZB, at 100 m) can differ by about 5 degrees. However, the difference is not sufficiently regular to be considered as a static bias, nor is there any evidence of changing behaviour with time, as can be seen in the sample time series. A scatter plot of the wind directions indicates excellent agreement between the two measurement sources. The differences observed between the two buoys are within the measurement uncertainty of the direction sensors, and may reflect actual differences between the two locations at each time step. The fit has a slope near unity, but deviates slightly from 1.0 due to the 5 degrees shift. The temporal differences are not seen in the average wind roses, which are nearly identical between HKZA and HKZB, at 100 m. Please find additional information in the memo, on the right in field H. | Memo combined WRA questions
35 | General | Combined Wind Resource Assessment | Concurrent mean wind speed | The concurrent mean wind speed (i.e. when measurements for both locations HKZA and HKZB are valid) differ by 0.1 m/s. Is there any explanation, given the small distance between the 2 positions? | 2017-11-27 | The dataset used for the combined wind resource assessment from the two LiDAR buoys includes recorded concurrent wind speeds over a 12-month period (05/06/2016 to 04/06/2017). The mean wind speeds recorded at 100 m over that period differ by 0.1 m/s in the raw data. However, the difference is primarily due to differences in the data availability for each LiDAR buoy. The HKZA buoy has a lower availability than HKZB. After quality control, and considering only time steps with concurrent measurements of both buoys, the mean wind speeds at 100 m differ by only 0.01 m/s. This level of accuracy is well within measurement uncertainties. Please find additional information in the memo, on the right in field H. | Memo Combined WRA questions
34 | General | Metocean Measuring Campaign | Reports | Until today (29/9), measurements from 5-6-2016 up to 5-6-2017 have been published from the metocean measuring campaign. Are there more expected to become available online, if so when? | 2017-10-16 | The June report has been published at 6-10-2017; http://offshorewind.rvo.nl/file/view/53714502/data-reports-june-2017-fugro. The measurement campaign started in June 2016 and will continue until January 2018. Reports are planned to be disclosed within 2 months after the ending of each month.
33 | General | Metocean Measuring Campaign | Data disclosure | It appears that data from the onsite wind measurement campaign is only available until April (approx. 2 months time delay). Is it possible to access the latest data? | 2017-07-06 | In order to have 12 months of consecutive measurements available as soon as possible, RVO.nl has decided to disclose also the first days of June 2017 in the May 2017 report. The results will be disclosed after the quality check and approval within 6 weeks after the end of the period.
32 | General | Bird Observation System | Costs Bird Observation System | According to article 4.3.b of the draft WFSD, “a system that effectively observes actual bird migration“ will be installed. The permit holder has to allow for the connection of that bird observation system with the control system of the wind turbines. However, it is unclear who has to install the bird observation system and bear the associated costs – either the permit holder or the Ministry of Economic Affairs. Is the bird observation system included in the environmental monitoring and evaluation programme that will be implemented by the ministry (see article 5.1 of the draft WFSD)? | 2017-06-27 | The location of the bird radar system is not yet known. It could be on the TenneT platform or on (a) wind turbine(s). The costs for the bird radar system are on the account of the government. If the system is to be installed on (a) windturbine(s), then it is mandatory that the permit holder cooperates with the government and gives access to the wind turbine(s) for the installation and maintenance of the bird radar system.
31 | General | Decommissioning | Decommissioning Start | In section 5.3.3 on page 51 in the Project & Site Description it is stated that: “Decommissioning can start latest end of year 25 and should be completed within two years maximum after the power generation operations have stopped, but at the latest in the 30th year.” Can you clarify if the sentence is correct or should it state “Decommissioning can start no earlier than end of year 25…”? | 2017-06-16 | The description in the Project and Site Description (PSD) is not correct. The sentence: “Decommissioning can start latest end of year 25 and should be completed within two years maximum after the power generation operations have stopped, but at the latest in the 30th year.” Must be replaced by: “Decommissioning can start end of year 25 earliest and should be completed within two years maximum after the power generation operations have stopped, but always within the term of the validity of the permit, in this case in the 30th year.” We will correct the PSD accordingly.
30 | General | Construction of the wind farm | Regulations during construction | These questions concern the regulations during the construction of the offshore wind farm: 1) Is a guard vessel to secure the construction site and passing traffic mandatory? 2) With reference to the Water Decree, art. 6.16h: Who is responsible for identification marks and beacons of the construction site? 3) Who pays for guard vessel(s), identification marks and beacons? | 2017-05-15 | 1) During construction activities guard vessel(s) are mandatory, at least one, in many cases two. This is subject to approval by the Netherlands Coastguard. 2) The site developer is responsible for the identification marks and beacons of the construction site. 3) The costs for guard vessel(s), identification marks, beacons and the mandatory Notice to Mariners are at the expense of the site developer.
29 | General | Metocean Study | Turbulence intensity | This is a question to the Metocean study on Hollandse Kust Wind Farm Zone: Chapter 10.1.4 Conversion between time scales: You are recommending the ISO 19901 wind spectra (Frøya spectra). You are recommending the same turbulence intensity at both 10 and 100 m above mean sea level? Then you will end up with too strong gust at the heights above 10 m? There is no doubt that wind turbulence shall decrease with height? That means that Figure 10.4 and Table 10.7 only is valid 10 meter above mean sea level? This table is used to calculate wind gust at all heights. In my opinion a 1-hour mean wind speed at 100 m of 39.6 m/s corresponds to 10-minute mean of 42.0 m/s (you have 44.3 m/s) and a 3 s gust of 49.2 m/s (you have 58.3 m/s). Can you please clarify? | 2017-05-12 | Your observations are correct. Netherlands Enterprise Agency and DHI have issued a revised report that has been made public on May 11th, 2017. Please refer to PDF page 16 ‘Revision History’ for the comparison between V2.2 and V2.1. Data in the Metocean Database are correct and do not need an update.
28 | General | Floating LiDARs | Location; serial numbers;listed serial | We have been unable to find the following information on the RVO web pages regarding the Hollandse Kust floating Lidars. Please could you provide the following information: 1) Confirmation of the location of both HKZA and HKZB in Lat/Long; 2) Confirmation of both of the device’s serial numbers; 3) The serial listed in the header of the HKZA file notes it as being “WS149”, however this corresponds to the FLiDAR1 at Borssele. As the time series for these two devices overlap it seems unlikely that they are the same device. | 2017-05-04 | Please find confirmation of the locations: a) In the Fugro Monthly Data reports. Locations can be found in paragraph 1. Introduction. b) In the Deltares Monthly Validation reports. Locations can be found in paragraph 1. Introduction. 2) The serial numbers of the devices which have been used can be found in the reports and data. Please note that -due to buoy swaps- positions can change in time within Wind Farm Zones (Hollandse Kust (zuid) and Hollandse Kust (noord)) and between Wind Farm Zones (Borssele, Hollandse Kust (zuid) and Hollandse Kust (noord). 3) WS149 is used in Borssele Wind Farm Zone, Hollandse Kust (zuid) and in Hollandse Kust (noord). WS149 is only used at one location at the time.
27 | General | Wind Resource Assessment | Correcting coordinates | Regarding table 13, page 36 of the HKZ Wind Resource Assessment (HKZ_20161222_Ecofys_Hollandse Kust (zuid) Wind Resource Assessment-F.pdf), can you please check the coordinates HKZ2 and HKZ4? | 2017-04-06 | The coordinates for points HKZ2 and HKZ4 prove to be inversed in Table 13. That error is also reproduced in the header for the Excel spreadsheets for points HKZ2 and HKZ4. The error does not affect any of the data or calculations. All results presented in the report and spreadsheets are correctly identified by site name. The metadata will be updated in a revised excel file and report.
26 | General | Inactive cables | Possible restrictions | Please clarify if there are any restrictions in relation to the inactive cables located in HKZWFS? | 2017-04-06 | There are no restrictions in relation to inactive / abandoned cables.
25 | General | Construction vessels | Positioning of construction vessels | Please clarify if positioning of construction vessels (including jack-ups and anchors) during site construction outside the HKZWFS boundary lines is allowed? | 2017-04-06 | This is allowed if positioning (jack-up and anchoring) is done in open sea. Positioning in maintenance zones or safety zones of existing cables and/or pipes and/or installations is prohibited unless agreed upon otherwise in a proximity agreement with the owner.
24 | General | Maintenance Zone | Positioning of anchors | Please clarify if positioning of anchors in the maintenance zones during site construction is allowed. If not, is positioning of anchors on the opposite side of the maintenance zone allowed with free positioning of the anchor cables in the maintenance zone? | 2017-04-06 | Anchoring in the maintenance zone of an existing cable or pipe is prohibited, unless agreed upon otherwise in a proximity agreement with the owner of the cable or pipe. Whether anchoring on the opposite side of the maintenance zone is allowed depends on the area. If this is open sea then anchoring is allowed, for the anchoring cables there is no restriction
23 | General | Final Wind Farm Site decisions | Appeals | Have appeals been made against the final Wind Farm Site Decisions WFS I and II Hollandse Kust (zuid)? If so, can you disclose who did so and on which basis? | 2017-03-09 | Seven parties have made an appeal at the Council of State. More information is to be found here: http://www.rvo.nl/subsidies-regelingen/bureau-energieprojecten/lopende-projecten/windparken/woz-kavels-holl-kust-zuid-i/i (Dutch only)
22 | General | Scour conditions | Scour conditions | Can you describe scour conditions to be expected at Hollandse Kust (zuid) for typical structure types (like monopiles)? | 2017-02-23 | The Netherlands Enterprise Agency will prepare for a concise report on scour conditions to be expected at Hollandse Kust (zuid), to be published Q2 2017.
21 | General | Planned COAM cable | Details on the COAM cable | Could you please provide more details on the planned COAM cable, hereunder planned installation schedule and any associated potential implications and/or interfaces during the construction and operation of the HKZI & II wind farms? | 2017-02-07 | The planning of the installation of the consented COAM telecom Cable, owned by PiPiper, is currently unknown.
20 | General | Metocean Data | Metocean timeseries | I have a question related to the Metocean data available for the Hollandse Kust (Zuid) site. For this site only Metocean reporting is available while for the Borssele sites also data in timeseries (from hindcasting) is available. These are the timeseries used to calculate the normal sea states and contain amongst others: wave height Hs, wave period Tp, wave direction, wind direction, wind speed. Would it be possible or is it planned to make these timeseries also available for Hollandse Kust (Zuid)? The availability of these timeseries would allow for a more detailed design assessment, reduce design conservatisms and therefore benefit the design of the support structures. | 2017-01-26 | These time series will be available through the metocean database. This metocean database will be published beginning of February 2017 and can be accessed from offshorewind.rvo.nl
19 | General | Site coordinates | Differences in coordinates | Two coordinates in the official Wind Farm Site Decision differ from those in Annex C: Boundaries and Coordinates (Part of Project and Site Description). | 2017-01-20 | The coordinates in Annex C: Boundaries and Coordinates (Part of Project and Site Description) and the Base Map (GIS.MPK file) are correct. There is an error in the publication of the Wind Farm Site Decision published in the Gazette on 16th December 2016. A rectification has been published in the Gazette of 20th January 2017 (in Dutch): Subject: Coordinates of the infield cable entry zone HKZWFS I: Point No. CE_02 Easting must be 571,497.2 and not 571.492,2. Point No. CE_05 Northing must be 5,797,511.9 and not 5.795.511,9
18 | General | Site coordinates | Differences in coordinates | We have noticed a discrepancy between the published draft Wind Farm Site Decisions I & II Hollandse Kust (zuid) and the PSD Appendix C: 'Boundaries and Coordinates version November 2016'. Which set of coordinates should be considered leading? | 2016-12-09 | The PSD Appendix C: 'Boundaries and Coordinates version November 2016' shows some small deviations from the draft Wind Farm Site Decisions. The coordinates in the final Wind Farm Site Decisions will be based on this memo. Nevertheless only the official final Wind Farm Site Decisions are legally binding and are expected to be published in December 2016.
17 | General | Windturbines and weather circumstances | Certification | The Water Decree states in article 6.16g: Section 6.16 that a wind turbine and any other part of the wind farm must be sufficiently strong. A statement about this must be compiled by an independent expert who has carried out tests in accordance with a proven system of standards relating to the design and installation of a wind farm.Can you enhance on the interpretation and the link to the project certification? Which Certification Bodies will be accepted as independend experts? | 2016-12-02 | Paragraph 1, section 6.16g can be covered by the certification phases design, which relies on the design basis (‘design basis’ and ‘design’ in diagram below). Paragraph 2, section 6.16g demands to prove that the construction/installation is safe before going into operation. For this purpose certification phases ‘manufacturing’, ‘transport & installation’ and ‘commissioning’ are designed. See diagram above. E.g. within DNVGL-SE-0190, for each certification phase a Statement of Compliance can be provided. In this way also the progress can be documented. The wind power plant assets to be covered within 6.16g are the wind turbines and the infield cables. The substation, export cables and control station are not covered within 6.16g. The certification body must be independent. It is industry standard to use a certification body accredited by a European national accreditation body. Certification by a non-accredited body will not be accepted.
16 | General | Safety zones | Jack-up operations | Please clarify if jack-up operations within the 500 m safety zone are allowed during installation of the wind farm as well as during the operational phase for potential repair and maintenance works? | 2016-11-11 | Jack-up operations are allowed in your own safety zone but prohibited in a maintenance zone of an existing cable or pipe. When a safety zone overlaps a maintenance zone, jack-up operations are prohibited unless agreed otherwise in a proximity agreement.
15 | General | Water Decree; transformer station | Certification of transformer station | The Water Decree includes two articles about the certification of a substation. Please explain if the future operator of a wind farm should submit design certificates covering the transformer station. | 2016-11-11 | Developers and operators of future wind farms are not responsible for the (TenneT) platforms (transformer stations). The text referred to applies to existing wind farms only.
14 | General | UXO removal by contractor | UXO removal by contractor | Who is allowed to remove UXOs and who is bearing the costs? | 2016-11-11 | Royal Netherlands Navy is solely responsible for the disposal (removal) or relocation of any UXO encountered. Other contractors are not allowed to do so. The authorities cover the cost of UXO removal.
13 | General | Requirements | Operational modifications | In Germany, new wind farms are required to modify operations of those turbines whose wake effect would exceed the assumptions used in designing previous installed wind farm(s). Does the Netherlands have now, or does it plan to have, a similar requirement as in Germany? | 2016-11-11 | There are currently no similar requirements foreseen.
12 | General | Crossing and proximity agreements | Private agreements required? | Are crossing and proximity agreements or any other agreements private law required with regards to the offshore wind farm? | 2016-11-11 | Crossing, proximity and any other agreements under private law are not mandatory.
11 | General | Soil samples | Future use soil samples | Will the soil samples from the geotechnical boreholes at the HKZ site be stored for future use? If so, for how long? | 2016-11-11 | The remaining samples will be stored until the winners of the tenders are known, and handed over to them.
10 | General | Wind Farm layout | Yield optimisation | Can you please confirm that the developer – with respect to project area borders, safety zones, etc. – has full freedom to make a wind farm layout based on yield optimisation; for example a curved layout or with a dense border of turbines versus a layout where turbines are in straight lines? | 2016-11-11 | Confirmed. There will be no other restrictions to the wind farm lay out other than the general rules and the design envelope. Restrictions to the lay out itself are not foreseen.
9 | General | Wind Farm Site Boundaries | Distance to boundaries | The Wind Farm Site Boundaries are not always exactly 500 metres from a cable, does this have any impact? | 2016-04-15 | The boundaries of the Wind Farm Sites as published in the Wind Farm Site Decisions are binding. For telecom cables a maintenance zone of 1,000 metres applies. In some cases the telecom cables and pipelines are not exactly in the middle of this maintenance zone due to small bends.
8 | General | Certification | Project certification body | Will there be a project certification body or comparable entity involved over the lifetime of the project, by some sort of periodic inspections? | 2016-02-23 | This is not foreseen.
7 | General | Standards and guidelines | Standards and guidelines | Which standards, recommendations, guidelines, obligations are to be followed for design, manufacturing, installation, commissioning and operation of the WTG, Foundation, Cable, interfaces? | 2016-02-23 | Internationally recognised standards. It is not possible to present a complete overview.
6 | General | Water Decree | Ministerial Order | Article 6.16g (4) of the Water Decree says "A ministerial order may lay down rules on the content of a declaration referred to in the second paragraph." Does such ministerial order, or a draft or a term-sheet, already exist? | 2016-02-23 | No, it does not. A brief guideline will be drafted that outlines which data in the various plans has to be submitted.
5 | Studies | Archaeology | Exclusion zone | Are you able to inform about the size of the exclusion zone around a potential object of archaeological value? | 2016-02-22 | In general a buffer or safety zone of 100 metres around an archaeological object or an object with an archaeological expectation is to be defined, in which no activities such as trenching or anchoring are allowed. If additional research shows that the object has no archaeological value, the location and the buffer zone can be omitted.
4 | General | Water Decree | Cables burial depth | Are there any requirements for inter array cables burial depth? The Water Decree only specifies this for Export cables to be 1.0 meter. Would the developer for instance be allowed, if preferable from a risk perspective, not to bury the cables? | 2015-12-10 | There are no requirements for the burial depth of inter array cables.
3 | General | European Species Licence | European Species Licence | Will a European Species Licence be required for any impact piling work or does the Kavelbesluiten cover any such requirement determined by the Habitats Directive? | 2015-12-10 | The Wind Farm Site Decision covers all requirements. No other permits / consents are needed.
2 | General | Water Decree | Export cables | Within the Water Decree there are a number of conditions stated for “export cables”. Please can it be confirmed that the term export cable only refers to TenneT cabling and the term does not include inter-array cabling within a wind farm? | 2015-12-10 | Confirmed.
1 | General | Wind farm layout | Procedure lay out approval | In case of any layout requirements the Tenderer needs to have his layout approved by the competent authority before tender submission in order to submit a firm bid as layout restrictions will impact the business case. What will be the procedure for layout approval during the tender process? | 2015-05-22 | The bandwidth and other restrictions defined in the wind farm site decision must be respected. There is no pre-approval procedure foreseen.